{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["Sheet1"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":129,"n_cols":9,"rows_kept":129,"merged":[[0,0,0,8]],"flags":["formulas_cached_only"]}
["龙华应急管理局2019年第二批双随机执法情况公示表"]
["序号","企业名称","企业地址","执法部门","执法人员","检查日期","检查情况（发现隐患问题）","整改情况","是否立案"]
[1,"深圳市君信和科技有限公司","深圳市龙华区龙华街道富康社区梦丽园工业区6栋厂房A栋4层403","龙华应急管理局","翟世明,谢立镇","2019-02-13","1.公司内一处安全出口门上方无“安全出口”标志；2.打包区内一处通往室外的安全出口门未采用防火门；3.打包区内一处安全疏散通道被货物占用；4.未按规定配备安全管理员；5.未将安全培训工作纳入本公司2019年度工作计划，检查时未制定2019年安全培训计划和公司工作计划；6.未建立事故隐患排查治理制度；7.未建立安全生产责任制；8.未建立从业人员安全培训档案。","已整改","是"]
[2,"深圳市龙昌盛印刷有限公司","深圳市龙华新区老围第二工业区E栋3楼","龙华应急管理局","翟世明,张键","2019-02-14","已搬迁",null,"否"]
[3,"深圳诺田科技有限公司","硅谷动力清湖园A15栋4楼","龙华应急管理局","林跃辉,章胜旗","2019-02-14","1.未制定2019年度安全生产工作计划","已整改","否"]
[4,"佛山市君百意自动化控制设备有限公司深圳分公司","深圳市龙华新区龙华街道和平路21号振华时代广场312","龙华应急管理局","黄智勇,章胜旗","2019-02-14","1、未建立事故隐患排查治理制度","已整改","否"]
[5,"深圳慕佳寝室用品有限公司","大浪街道华荣路46号东龙兴科技园5号厂房1楼","龙华应急管理局","钟汉林,吴明明","2019-02-14","1、仓库货物是否堵塞消防通道，仓库是否未划分标示线。2、升降架使用时护栏是否未关闭，是否未张贴警示标志。3、仓库灭火器配备是否充足。","整改中","否"]
[6,"深圳市志达成模具科技有限公司","华繁路泉新源工业区1栋1楼","龙华应急管理局","杨远辉,彭育文","2019-02-14","1、电箱下方杂物。2、磨刀机操作台未安装地线。3、CNC员工未佩戴劳保耳塞。","整改中","否"]
[7,"深圳市康富来机电有限公司","大浪街道华荣路351号金瑞中核工业园4栋1层东","龙华应急管理局","吴明明,杨远辉","2019-02-15","1、CNC员工、铣床员工未佩戴劳保用品（耳塞、护目镜）。2、锯床机械设备未安装漏电保护开关。","已整改","否"]
[8,"深圳市哲科乐创科技有限公司","深圳市龙华区福城街道沃特斯科技园2栋4楼E区","龙华应急管理局","罗兆麟,罗中宝","2019-02-18","1.车间内部分插座未接地保护；2.车间与仓库之间未进行防火分隔；3.车间灭火瓶及消防栓未按时进行点检。","已整改","否"]
[9,"深圳市友创绝缘材料有限公司","大三社区大三村桔黄工业区367号-7","龙华应急管理局","江志豪,宋煜竹","2019-02-18","1.三楼生产车间部分电源箱未张贴安全警示标志；2.一楼模压车间部分插座相零线接反；3.一楼仓库与办公区域混合设置在一起存在二合一现象。","已整改","否"]
[10,"禹鸿展塑胶电子（深圳）有限公司","深圳市龙华区福城街道大三社区大三村259-34号三，四、五层","龙华应急管理局","罗中宝,罗兆麟","2019-02-18","该企业车间无人上班，已停产停业准备搬迁，车间内生产设备原有13台注塑机，已卖掉8台，剩余5台注塑机已断电待处理，并承诺3月15日前搬迁处理完毕。","停产停业","否"]
[11,"深圳市创展电子科技有限公司","章阁社区松源创新科技城B栋8F西边","龙华应急管理局","江志豪,冼耀行","2019-02-18","1.八楼生产车间危险化学品分装容器未张贴安全警示标识，未设置防泄漏装置；2.八楼生产车间金属架工作台未做地线跨接；3.八楼生产车间消泡机安全阀与压力表未定期进行检测；4.八楼生产车部分电源箱未张贴安全警示标志；5.八楼生产车间磨边机除尘管道使用非导静电软管。","已整改","否"]
[12,"日成协和模具（深圳）有限公司","深圳市宝安区大浪街道高峰社区日成协和厂房3栋一楼","龙华应急管理局","饶慧彬,胡辉","2019-02-18","经现场检查，该企业已停业停产",null,"否"]
[13,"深圳市赛瓦特动力科技股份有限公司","大浪街道华昌路","龙华应急管理局","钟汉林,饶慧彬","2019-02-18","经现场核查该企业已搬迁。",null,"否"]
[14,"深圳市欣开泰科技有限公司","深圳市龙华区大浪街道大浪南路445号德爱工业区A栋3楼","龙华应急管理局","高扬凯,杨晓鹏","2019-02-19","1、工字电感接脚机女操作工操作期间为佩戴工作帽；2、工字电感接脚机传动轮部位防护罩缺失；3、灭火器设置点存放量过多；4、车间组配电箱未安装漏电保护开关，未安装屏护板；5、接地线、零线未使用接线端子连接。","整改中","否"]
[15,"深圳市鑫恒锋模具有限公司","深圳市龙华区大浪街道浪口社区浪口工业园（青年梦工场）二栋一楼102","龙华应急管理局","傅霏,霍松涛","2019-02-19","1、行吊设备未进行定期检测；2、铣床电锯防护装缺失置；3、电气插座未安装地线。","已整改","否"]
[16,"深圳市富鑫通办公用品有限公司","龙华新区龙华办事处油松华雅工业园华雅工业园B区102","龙华应急管理局","章胜旗,陈洪星","2019-02-19","1.生产车间电箱下堆放货物；2.生产车间一处安全出口未安装出口指示标志；3.未将事故隐患排查治理情况如实记录。","已整改","否"]
[17,"深圳振翔通科技有限公司","深圳市龙华新区大浪街道新岭路忠诚工业园A3A5区办公楼3楼","龙华应急管理局","吴海志,石元知","2019-02-19","经现场检查该企业已搬迁。",null,"否"]
[18,"深圳市华茂电线电缆有限公司","罗屋围黄档路2号7楼A1区","龙华应急管理局","彭宇新,罗雨锋","2019-02-19","经现场核查该企业已搬迁。",null,"否"]
[19,"深圳市海奥斯硅胶制品厂","南江工业区第二栋一楼103","龙华应急管理局","彭胜勇,许爱关","2019-02-19","经现场核查该企业已搬迁。",null,"否"]
[20,"深圳市华创精细电子有限公司","深圳市龙华新区大浪街道华荣路旁联建科技工业园厂房4栋1层","龙华应急管理局","庞海锋,许伟彬","2019-02-19","1.生产车间贴片机、波风焊未张贴岗位风险辩识告知卡；\n2.危险化学品存放防爆柜内无防泄漏托盘，未张贴安全风险辩识告知卡；\n3.仓库灯具未按规定配置防爆灯；\n4.生产车间、仓库部分安全出口未按规定配置安全出口警示标识及应急照明灯；\n5.生产车间部分机械设备点检记录未及时更新；\n6.生产车间机械设备未张贴机械设备预防伤害“十一条”铁律。","已整改","否"]
[21,"深圳市力晟通科技有限公司","深圳市龙华新区大浪街道华宁路5号2楼201","龙华应急管理局","许伟彬,彭育文","2019-02-19","经现场核查该企业已搬迁。",null,"否"]
[22,"深圳市鹏创物联技术有限公司","大浪街道华悦路132号2楼","龙华应急管理局","吴明明,曾令才","2019-02-19","1.办公场所内少量测试电芯乱堆放，未设防爆柜管理存放；2.办公场所内少量危化品（白电油）乱堆放，未设防爆柜管理存放；3.仓库灯具（日光灯）未作防爆处理4.焊锡工作台未安装抽风系统；5.部分灭火器材点检表未及时更新。","已整改","否"]
[23,"深圳市鑫旭飞科技有限公司","深圳市龙华新区大浪办事处同胜社区金龙路南江工业区第二栋4楼","龙华应急管理局","许伟彬,彭宇新","2019-02-19","经现场核查该企业已搬迁。",null,"否"]
[24,"深圳市中通创安科技有限公司","观澜街道大和社区大和村596号怡力科技园A栋3梯2楼","龙华应急管理局","高俊丽,陈伟聪","2019-02-20","1、车间部分危险化学品(酒精)容器没有张贴安全警示标识；2、车间一安全出口上班时间上锁。","整改中","否"]
[25,"深圳市格隆精密五金有限公司","深圳市龙华区观湖街道观平路189号金常盛工业区E栋3楼A区","龙华应急管理局","陈伟和,廖志城","2019-02-20","1.灭火器配备不均匀；2.灭火器下堆放货物；3.砂轮机未安装漏电保护开关；4.员工在生产车间抽烟；5.仓库电气未作防爆处理。","整改中","否"]
[26,"深圳市好温馨家用纺织品有限公司","深圳市龙华区观湖街道樟坑径社区牛角龙工业区A8栋一楼南端、二层、三层","龙华应急管理局","张艺馨,陈家雄","2019-02-20","1、消防栓下货物堵塞。\n2、车间部分电源箱未进行静电跨接，缺少保护面板。\n3、消防灭火器未定期检测。","整改中","否"]
[27,"新信嘉服装（深圳）有限公司","深圳市龙华新区观澜老村社区腾龙工业区新腾路6号第2栋2楼，第3栋1楼","龙华应急管理局","黄桂明,张艺馨","2019-02-20","1.灭火器未定期维护保养；2.部分电源箱未张贴警示标志；3.大功率风扇间隙过大未安装漏网；4.部分电源线裸露未套管。","已整改","否"]
[28,"深圳市富城精密塑胶模具有限公司","深圳市龙华新区观澜街道樟坑径社区下围工业区一路6号D栋一楼 ","龙华应急管理局","万可明,许斌宇","2019-02-20","1.火花机未张贴安全操作规程；2.钻床未张贴维修保养记录；3.部分电源开关缺失防护罩。","已整改","否"]
[29,"深圳市泽天包装制品有限公司","大浪同富邨工业区5栋2楼","龙华应急管理局","彭胜勇,石元知","2019-02-20","1、车间下角料未设置独立区域存放，2、配电箱下方堆放杂物，须清理，3、配电箱未安装漏电保护装置，4、车间部份电线外露，5、圈占消防栓一处，6、临时中转仓库上方电气未作防爆处理，","整改中","否"]
[30,"深圳市富尔宝沃科技有限公司","深圳市龙华新区大浪街道浪口社区浪口工业园89号4楼405","龙华应急管理局","罗雨锋,许伟彬","2019-02-20","1.该企业生产部已撤离未作生产，现主要用途作办公使用。",null,"否"]
[31,"深圳市雄飞精密五金机械有限公司","深圳市龙华区龙华街道华联社区河背工业区河盛文创园厂房1楼","龙华应急管理局","邱定南,翟世明","2019-02-21","1.生产车间与办公区采用普通玻璃分隔；2.生产车间5号数控车床进料口保护装置缺失；3.未开展节后复工复产前各项安全生产工作；4.未制定公司2019年年度安全培训计划；5.未将事故隐患排查治理情况如实记录，也未向从业人员通报。","已整改","是"]
[32,"深圳市亿凯电子元件有限公司","深圳市龙华新区龙华街道和平东路港之龙科技园商务中心C座504室","龙华应急管理局","黄智勇,章胜旗","2019-02-21","1、仓库内电线路乱拉乱接。2、安全出口堆放货物。","已整改","否"]
[33,"深圳市瑞林电子科技有限公司","深圳市龙华新区观澜街道上坑社区上围工业区2000032栋402","龙华应急管理局","胡基立,陈镇江","2019-02-21","经与管理处核实该企业已搬迁","企业已搬迁","否"]
[34,"深圳市恒鑫利橡塑材料厂","深圳市恒鑫利橡塑材料厂","龙华应急管理局","陈镇江,陈小龙","2019-02-21","1.车间部分电箱未张贴警示标志及五楼部分插座未安装地线；2.四楼车间烤箱未作考评报告；3.四楼丝印车间电气未作整体防爆且可燃气体浓度报警器未安装在有人值守的地方；5.五楼部分电线未套管保护；6.五楼喷漆车间未安装可燃气体浓度报警器且未电气设备未作整体防爆；7.五楼喷漆车间煤油随意乱放；8.四楼车间插座安装在木板上，未用绝缘板分隔。9、五楼车间部分电源未安装地线。","整改中","否"]
[35,"深圳市利通连接器有限公司","深圳市利通连接器有限公司","龙华应急管理局","胡基立,周熠珊","2019-02-21","1、车间部分电源箱未张贴用电安全警示标识；2、车间部分电源箱箱盖未与箱体作静电跨接;3、未完善2019年安全生产管理制度。","整改中","否"]
[36,"深圳市旋彩电子有限公司","深圳市龙华新区观澜下湖社区下围工业区一路1号3楼A区","龙华应急管理局","林耿宇,邓旭洋","2019-02-21","1.部分危险化学品（酒精）分装瓶未张贴安全标签;2.设备未定期进行维修保养;3.焊线车间部分员工未佩戴劳动保护用品;4.烤箱未做年度性能安全检测，未张贴安全警示标志;5.消费器材未定期检查，检查记录未健全;6.部分车间金属工作台未接地","已整改","否"]
[37,"深圳市群盈塑胶有限公司","深圳市龙华区福城街道丹湖社区润塘工业区78号","龙华应急管理局","刘杭科,吴宏宇","2019-02-21","1.未按要求划设明显安全标线；2.机械设备未安装末端漏电保护器，地线安装不规范，未张贴风险告知牌，无维修保养记录；3.在通道处设置动火作业区，不符合要求；4.未在有较大危险因素的生产经营场所（配电房）设置明显的安全警示标志；5.配电房内未配备劳动防护用品和应急处置工具；6.车间总配电箱未安装二级漏电保护器，箱内未设置地线端子；7.在宿舍一楼设置仓库；8.工作台照明灯未接地保护。","已整改","是"]
[38,"深圳市兴科安电子技术有限公司","浪口社区华荣路鹏腾达工业园2栋2楼","龙华应急管理局","庞海锋,彭育文","2019-02-21","1、生产车间未装乙防火门。\n2、少量危险品（酒精）未设防爆柜存放。","整改中","否"]
[39,"深圳市鑫宝龙电子厂","新围第三工业区G栋3楼","龙华应急管理局","庞海锋,邓国鸿","2019-02-21","1.车间设置办公区，存在二合一，2.车间通道货物乱堆放，3.车间部分防火门未安装闭门器，4.危险化学品无责任人信息，无安全技术说明书，5.仓库未按五距要求摆放货物。","整改中","否"]
[40,"深圳市凯菲隆贸易发展有限公司","深圳市龙华新区龙华昌永路和平工业园金星大厦4楼401室","龙华应急管理局","谢立镇,翟世明","2019-02-22","1.货品储存区安全疏散通道、安全出口被货物占用、阻挡；2.办公区与仓库（货品储存区）之间采用普通玻璃分隔；3.前台门口配电箱及电气设施被货物圈占；5.货品储存区内一向安全出口门在上班时锁闭；6.未将事故隐患排查治理情况如实记录、并向从业人员通报；7.未制定2019年度公司安全培训计划。","整改中","否"]
[41,"深圳市智上联合智能科技有限公司","深圳市 龙华区 龙华新区 观澜街道环观中路282号B栋2-4楼","龙华应急管理局","林耿宇,张艺馨","2019-02-22","1.不具备锂电池仓储条件；2.作业现场锂电池及带锂电池产品管理混乱；3.普通仓库存放带锂电池产品；4.未对事故隐患排查治理擅自组织生产经营。","整改中","是"]
[42,"深圳市嵘洲华鑫电子有限公司","深圳市龙华区观湖街道观城社区新岭工业区201-8","龙华应急管理局","陈伟聪,阳虎田","2019-02-22","1.车间通道被货物堵塞；\n2.车间物品堆放过高。","已整改","否"]
[43,"深圳市永远发电子有限公司","深圳市龙华新区观澜横坑社区环观中路河东厂房408号A栋左边一楼","龙华应急管理局","陈伟和,林耿宇","2019-02-22","1.从业人员未佩戴劳动防护用品；2.分级电源开关未安装漏电保护开关，且屏护板缺失；3.注塑机设备末端未安装漏电保护开关；4.消防器材未定期检查；5.生产车间未规范划线。","整改中","否"]
[44,"深圳市曹万和包装制品有限公司","环观中路六合科技园A栋5层A区西","龙华应急管理局","唐飞,邱毅彪","2019-02-22","1.部分化学用品瓶身未粘贴标签；2.电源开关下方对方杂物；3.部分安全生产制度未更新至2019年。","已整改","否"]
[45,"敏康光电科技（深圳）有限公司","深圳市龙华区福城街道桔塘社区桔岭新村洋金C栋4楼403","龙华应急管理局","陈志成,刘杭科","2019-02-22","1.四楼生产车间有一处插座未接地线；2.四楼生产车间安全出口使用卷闸门；3.四楼生产车间安全疏散通道堆放包装材料。","已整改","否"]
[46,"深圳市永佳和科技有限公司","深圳市龙华新区大浪街道创艺路16号瑞兴科技园A座1楼","龙华应急管理局","罗雨锋,吴海志","2019-02-22","1、安全出口门（1处）内开，不符合紧急疏散逃生要求；2、磨床（一台）无集尘装置；3、电箱（1处）无屏护板，箱门与箱体地线未跨接；4、铣床工未佩戴劳保用品（护目镜）；5、机械设备未张贴风险辨识告知卡。6、部分机械设备无操作规程和维修保养记录。","整改中","否"]
[47,"深圳市兆文纺织服装有限公司","深圳市龙华新区观澜街道桔塘社区大富路179号","龙华应急管理局","刘勤,廖名玙","2019-02-25","1、一楼丙类仓库内设置生产机器设备，办公室与仓库使用木门进行防火分隔；2、4楼个别配电箱未张贴安全警示标志，配电箱下堆放杂物；3、车间和仓库内灯光疏散指示标志设置数量不足；4、未按法律法规要求设置安全总监。","整改中","否"]
[48,"深圳市龙华区福城栋芳塑胶五金加工厂","章阁社区章阁老村C区268号","龙华应急管理局","刘勤,杨晓鹏","2019-02-25","已搬迁",null,"否"]
[49,"深圳市卓越求实电子有限公司","深圳市龙华区龙华街道幸福城润园三期13栋1402(清湖工业城鸿滔创客大厦4楼402)","龙华应急管理局","张键,陈洪星","2019-02-25","未建立事故隐患排查治理制度","已整改","否"]
[50,"深圳市蓝彩科技有限公司","深圳市龙华新区龙华街道民清路光辉科技园2栋2单元303","龙华应急管理局","章胜旗,邱定南","2019-02-25","1.仓库与办公区未设置防火门；2.仓库安全疏散通道标线模糊。","整改中","否"]
[51,"深圳市华万龙科技有限公司","深圳市龙华区龙华街道清华社区清龙路1号卫东龙工业园1栋4层","龙华应急管理局","翟世明,张键","2019-02-25","1、生产车间通道堆放货物。2、一处安全门闭门器损坏。","已整改","否"]
[52,"深圳蝶变智慧医用技术有限公司","深圳市龙华区龙华街道清祥路清湖工业园宝能科技园7栋A座7楼ABCDEF","龙华应急管理局","翟世明,张键","2019-02-25","1.数据机房、实验室与办公区采用普通玻璃分隔；2.仓库、网络机房未设置防火门；3.实验室部分电源线采用花线；4.网络机房内摆放大量纸箱杂物。","整改中","否"]
[53,"深圳市艾科诚科技有限公司","深圳市龙华新区龙华街道硅谷动力清湖园C2栋竟凯大厦317室","龙华应急管理局","张键,曾繁华","2019-02-25","1.未制定生产安全事故应急救援预案","整改中","否"]
[54,"深圳市泰尼科技有限公司","深圳市龙华区福城街道福民路168号福苑工业区2栋2楼","龙华应急管理局","杨能鹏,李宏桃","2019-02-25","1.二楼生产车间生产线电源插座未接地线；2.二楼生产车间部分电源插座未接地线。","已整改","否"]
[55,"深圳市凯安顺电子有限公司","深圳市龙华区福城街道茜坑四和社区茜坑路131号A栋3楼","龙华应急管理局","陈志成,黄国辉","2019-02-25","1.  三楼办公场所部分电源插座未接地线；2.三楼仓库部分货物随意摆放堵塞疏散通道；3.三楼测试岗位测试工作台未静电接地。","已整改","否"]
[56,"深圳市泉晶电子科技有限公司","深圳市龙华区福城街道茜坑新城社区竹村福庭工业区10栋6楼","龙华应急管理局","宋煜竹,李宏桃","2019-02-25","1.六楼包装车间工作台插座未接地线；2.六楼丝印车间部分电源线路未套管保护；3.六楼研磨车间玻璃研磨机电源控制箱保护盖缺失；4.六楼生产车间部分电源控制箱未安装屏护面板；5.六楼研磨车间部分电源线路“乱拉乱接”未套管保护，且使用花线。","已整改","否"]
[57,"深圳市龙华新区观澜忠辉五金制品加工厂","深圳市龙华区福城街道茜坑社区福苑工业区168号铁皮房4栋1楼中间","龙华应急管理局","黄国辉,刘杭科","2019-02-25","1.一楼生产车间部分电源插座接地故障；2.一楼生产车间机械设备未接地线；3.一楼生产车间部分冲床未安装双手同步按钮。","已整改","否"]
[58,"深圳市东涛机电设备有限公司","茜坑新城社区福庭工业区2栋一楼东面","龙华应急管理局","吴宏宇,罗兆麟","2019-02-25","1.机械设备点检记录缺失；2.生产车间安全疏散标志淡化失效；3.生产车间临时用电均未设置接地保护；4.生产车间东侧墙壁上部分控制开关缺少漏电保护器；5.生产车间杂物堆积，未划分区域功能线，部分杂物堵塞应急疏散通道；6.生产车间东侧出口应急灯损坏；7.车间电源控制开关保护盖上未张贴安全警示标志。","整改中","否"]
[59,"深圳市晟捷橡塑五金有限公司","深圳市龙华区福城街道新塘村76号易事达工业园201","龙华应急管理局","杨能鹏,杨伟森","2019-02-25","1.二楼生产车间缺少2019年机械设备维修保养记录；2.二楼生产车间未划分明显通道标识线；3.二楼生产车间消防栓存在圈占埋压现象；4.二楼生产车间烤箱控制电源箱被堵无操作空间。","整改中","否"]
[60,"深圳市兴雄昌塑胶五金有限公司","罗屋围第三工业区C栋1楼3分隔","龙华应急管理局","吴海志,幸小东","2019-02-25","1、生产车间未划线标识，2、生产车间圈占消防栓一处，3、生产车间电线外露，4、电源盒未粘贴安全警示标识，5、冲床设备未安装双手同步按钮，红外感应装置。","整改中","否"]
[61,"深圳市合盈嘉包装制品有限公司","深圳市龙华区观澜街道新田腾龙工业区120号三楼","龙华应急管理局","李勇,刘凌峰","2019-02-26","1.冲床机的安全防护装置失效，部分设备未张贴安全操作规程；2.原材料仓及废品仓与生产车间未进行有效防火分隔；3.灭火器点检不及时；4.仓库“五距”不符合要求；6.部分配电盒未张贴安全警示标志。","整改中","否"]
[62,"深圳市亨和恒电子有限公司","福民悦兴围英达利工业区5楼一半","龙华应急管理局","桂春林,刘勤","2019-02-26","1、丙类仓库和生产车间、生产车间和办公室防火分隔耐火等级不足；2、仓库内货物堆放杂乱，不符合五距要求；3、使用饮料瓶盛装危化品。","整改中","否"]
[63,"深圳市一格包装材料有限公司","横坑河西村","龙华应急管理局","赖嘉杰,马征涛","2019-02-26",null,null,"否"]
[64,"深圳市桥扬电子科技有限公司","深圳市龙华区观澜街道库坑泗黎路408号3楼301","龙华应急管理局","高扬凯,刘勤","2019-02-26",null,null,"否"]
[65,"深圳市洋明达科技有限公司","深圳市龙华区观湖街道观城社区大和村597号-3鑫潮工业园厂房101","龙华应急管理局","陈志聪,宋增","2019-02-26","1、车间部分线路乱拉乱接。","未复查","否"]
[66,"深圳市威达建材有限公司","深圳市龙华新区观澜街道观澜建材市场虎地排村102-3号","龙华应急管理局","王文斌,宋增","2019-02-26","1、消防通道堆放货物堵塞消防通道；\n2、电源箱盖缺失；\n3、电源箱下堆放杂物；\n4、未完善2019年企业安全管理制度；","未复查","否"]
[67,"深圳市鑫丰达皮具制品有限公司","观湖街道新田社区牛轭岭村224号401","龙华应急管理局","高俊丽,林耿宇","2019-02-26","1.黄胶和白电油分装容器上未张贴安全标签；2.使用黄胶等危险化学品的从业人员未佩戴符合国家标准的劳动防护用品；3.过胶机和钉扣机等设备皮带齿轮未安装防护罩；4.防爆柜放置在配电房门口、且静电接地不符合规范，未张贴危险化学品安全技术说明书；5.一安全出口未安装应急照明灯；6.部分电源开关未安装盖板；7.总电源开关箱未安装屏护板，房内未铺设绝缘脚垫等安全防护措施。","已整改","否"]
[68,"深圳市金灿坤科技有限公司","深圳市龙华新区观澜街道大水坑社区桔岭老村圣阳工业园厂房A2栋2楼右侧","龙华应急管理局","吴宏宇,刘杭科","2019-02-26","1.生产车间左侧安全出口未设置应急灯；2.企业在办公区域设置货物中转区域；3.生产车间抹机水盛装瓶未张贴简易安全标签。","整改中","否"]
[69,"深圳市桔栢科技有限公司","大水坑大二村大唐工业园A栋2楼南","龙华应急管理局","黄国辉,宋煜竹","2019-02-26","在大唐工业区管理处负责人段惠兰的陪同下进行检查发现该企业未开业，处于停产停业状态。","停产停业","否"]
[70,"深圳市利达兴激光刀模有限公司","元芬工业区B栋2楼","龙华应急管理局","吴海志,曾令才","2019-02-26","1.安全通道有杂物堆放堵塞安全通道.2.车间安全出口未安装消防应急指示灯。3.消防器材（灭火器）未定期点检。4.车间部分机械设备未张贴安全操作规程及维修保养记录。","整改中","否"]
[71,"深圳汉王友基科技有限公司","深圳市龙华区大浪街道华兴路5号富隆特工业园4栋3层西面","龙华应急管理局","朱剑峰,傅霏","2019-02-27","1.三楼工程实验室6处焊锡作业岗位未设置抽排烟装置；2.三楼配电房内堆放货物，配电箱下设置工作台，配电箱带电部位无屏护板。","整改中","否"]
[72,"深圳市丹顶鹤塑胶制品有限公司","龙华街道油松社区顺景大厦B座6楼B区（富士康南门附近）","龙华应急管理局","张键,曾繁华","2019-02-27","1、未将事故隐患排查治理情况如实记录；2、车间通道堆放货物。","整改中","否"]
[73,"深圳市旭博电子有限公司","深圳市龙华区观澜街道沙博工业区B栋四楼","龙华应急管理局","阳虎田,王文斌","2019-02-27","1.插件车间波峰焊设备无剩余电流保护装置；\n2.部分化学品分装容器未张贴安全标签；且化学品无安全技术说明书；\n3.打包机无操作规程；\n4.焊锡岗位员工未配备符合安全标准的防护用品。","未复查","否"]
[74,"深圳市丰祥瑞华电子科技有限公司","大水坑大一村沃特思科技园5栋4楼403","龙华应急管理局","黄强,朱子华","2019-02-28","（1）工作台未设置漏电保护开关，灯具未接地；（2）焊锡岗位员工未佩戴符合职业病防治要求的防护口罩；（3）被检查单位空压机压力表未进行检测。","整改中","否"]
[75,"深圳市鑫鑫鸿运五金制品有限公司","深圳市龙华新区观澜街道石马径社区君新路142-4号胜顺产业园C栋一楼东侧A","龙华应急管理局","朱剑峰,付勇","2019-03-04","1、车间钻孔机未设置安全操作规程；2、焊接区插座未设置接地保护；3、冲床操作工未佩戴防护用品。","已整改","否"]
[76,"深圳明冠家居有限公司","深圳市龙华新区观澜街道大水坑一村兴汉工业园B区一楼（桔坑路77号)","龙华应急管理局","朱子华,高扬凯","2019-03-04","已搬迁","整改中","否"]
[77,"全崴五金（深圳）有限公司","深圳市龙华新区观澜街道黎光社区黎光工业区第18栋","龙华应急管理局","刘勤,朱剑峰","2019-03-04","1、工作台安全灯违规使用220V工作电压驳接；2、排风扇皮带裂纹严重，排风扇表面污浊；3、二楼1具灭火器胶管裂纹。","整改中","否"]
[78,"深圳市欧力时尚科技有限公司","深圳市龙华新区观澜街道贵湖塘街1栋二楼","龙华应急管理局","刘勤,符桓彬","2019-03-04","1.灭火器未定期点检；2.危化品清洗剂未张贴安全标签;3.防爆柜内堆放杂物。","整改中","否"]
[79,"深圳市优快易国际供应链有限公司","深圳市龙华区民治街道办中华路24号广明工业园A2栋(厂房)1层","龙华应急管理局","郑江珠,余俊贤","2019-03-04","1.小办公室防火门闭门器缺失；2.小办公室出口处应急灯及出口指示牌缺失；3.仓库内后侧一应急照明灯失效；4.未按规定制定2019年年度安全教育培训计划并保证所需资金。","整改中","否"]
[80,"深圳市邦正供应链管理有限公司","深圳市龙华区民治街道办中华路康盛工业区117-119","龙华应急管理局","钟国峰,余俊贤","2019-03-04","1.防火门闭门器未正确安装；2.未如实记录从业人员安全教育培训情况","整改中","否"]
[81,"深圳市泛舟通信设备有限公司","建辉82号富联工业园2栋3楼","龙华应急管理局","陈洪星,黄智勇","2019-03-04","未制定2019年度安全生产工作计划","整改中","否"]
[82,"深圳市名鹭服饰设计有限公司","大浪街道大浪社区石龙仔路10号默根厂房105","龙华应急管理局","霍松涛,付勇","2019-03-05","1.一楼经营场所灭火器材配备不足，明显处无禁烟防火标志；2.一楼经营场所灭火器独具摆放在地面上，且灭火器压力不足，无月检记录；3.消防通道不暢通，行人通道设置台阶无警示标志。","整改中","否"]
[83,"深圳福林包装有限公司","深圳市龙华区福城街道大水坑社区大二村152厚德威厂房四102","龙华应急管理局","赖嘉杰,朱子华","2019-03-05","1、车间与仓库未做有效防火分隔；2、部分电气开关未张贴安全警示标识，部分电气开关盖板缺失；3、部分电气线路裸露未进行套管；4、货物堆放堵塞消防栓。","已整改","否"]
[84,"深圳市麦维普电子科技有限公司","深圳市龙华新区观澜街道茜坑社区茜坑路129号5号2楼","龙华应急管理局","傅霏,朱剑峰","2019-03-05","该企业共有员工3名，主要生产电子烟半成品组装，未涉及有使用锂电池。",null,"否"]
[85,"深圳市天杭科技有限公司","深圳市龙华区展滔科技大厦A座2307","龙华应急管理局","钱俊崇,房智锋","2019-03-05","1.办公室货物堆放混乱；2.未对从业人员进行安全生产教育培训，并留下相关记录。","整改中","否"]
[86,"深圳市维莎网络科技有限公司","民治街道梅板大道民乐科技园C栋403","龙华应急管理局","杨洋,赵吉飞","2019-03-05","1、已按要求配备应急照明灯及灭火器材。","无需整改","否"]
[87,"深圳市致优尚品科技有限公司","深圳市龙华新区民治街道梅坂大道民乐科技园创客工坊E栋605","龙华应急管理局","赵吉飞,余焕森","2019-03-05","1、灭火器材未定期检测。","已整改","否"]
[88,"深圳市大知云科技发展有限公司","深圳市民治牛栏前工业区28栋207号","龙华应急管理局","房智锋,张文龙","2019-03-05","1、安全出口未安装应急照明灯。","整改中","否"]
[89,"深圳华扬威视科技有限公司"," 深圳市龙华新区民治街道工业东路南侧泰明工业区一栋第二层A","龙华应急管理局","黄锡山,陈育平","2019-03-05","1、生产车间配电箱无屏护及跨接。","整改中","否"]
[90,"深圳市联之印科技有限公司","深圳市龙华新区民治街道工业东路南侧泰明工业区2栋4楼东侧","龙华应急管理局","张机敏,郑江珠","2019-03-05","1.灯下方堆放货物","整改中","否"]
[91,"深圳迈科联发科技有限公司","深圳市龙华新区龙华街道油松路146号梦丽园工业区6栋405号","龙华应急管理局","翟世明,邱定南","2019-03-05","1.仓库内设包装作业区，且安全疏散通道被货物占用；2.仓库内消防设施、电源开关与插座被货物圈占；3.新租用仓库未配备灭火器；4.办公区内堆放大量可燃杂物；5.未按规定配备安全管理人员；6.未建立安全生产责任制；7.未建立事故隐患排查治理制度；8.未将安全培训计划纳入本公司2019年度工作计划（检查核实未制定本年度公司工作计划与安全培训计划）；9.未将事故隐患排查治理情况如实记录、向从业人员通报（检查核实无记录无通报）；10.未按规定对从业人员进行安全培训教育。","整改中","是"]
[92,"深圳市兴同五金机械有限公司","深圳市龙华区福城街道茜坑四和社区茜坑路65号B栋1楼","龙华应急管理局","江志豪,罗中宝","2019-03-05","1.生产车间磨刀机末端未设置漏电保护开关；2.生产车间切割机未接地线，把手绝缘层缺失；3.灭火器安装高度过高，不符合规范要求；4.生产车间机械设备未张贴风险告知牌及操作规程。","已整改","否"]
[93,"深圳市立宇体育用品有限公司","深圳市龙华区民治街道西头工业区4栋","龙华应急管理局","钟国峰,余俊贤","2019-03-06","1.车间内机器设备（钻床）未固定；2.生产车间油漆未放置防爆柜内；3.机器设备（钻床）未制定日常保养记录和安全操作规程。","整改中","否"]
[94,"深圳市安卓安科技有限公司","民乐科技园雅星大厦405","龙华应急管理局","陈育平,赵吉飞","2019-03-06","、已配备应急照明灯及灭火器材","无需整改","否"]
[95,"深圳水滴润电子商务有限公司","民乐工业区D栋101-A","龙华应急管理局","林正权,杨洋","2019-03-06","1.仓库安全出口堆放货物","整改中","否"]
[96,"深圳市蒂森特电子科技有限公司","深圳市龙华新区梅坂大道民乐工业园雅星大厦607","龙华应急管理局","钱俊崇,陈乃稳","2019-03-06","1、已配备应急照明灯及灭火器材","无需整改","否"]
[97,"深圳市厚德铭电子有限公司","民乐科技园E栋413","龙华应急管理局","谢栓,房智锋","2019-03-06","1.灭火器未定期检查确保其完好有效","整改中","否"]
[98,"深圳市华塑装饰材料有限公司","深圳市龙华新区华达路7号彬香华工业园2栋2楼","龙华应急管理局","陈洪星,章胜旗","2019-03-06","1.生产车间一台晒板机未安装漏电保护器","整改中","否"]
[99,"神勇手袋（深圳）有限公司","深圳市龙华区观澜君新社区环观南路47号A栋3-4层","龙华应急管理局","彭佳亮,吴奕霖","2019-03-06","1.仓库内使用机械设备。2.机械设备齿轮转动部位未加盖保护。3.灭火器无点检记录。","整改中","否"]
[100,"深圳市建达玻璃制品有限公司","深圳市龙华区福城街道新城社区发得顺工业新村B3、B4、C6栋厂房","龙华应急管理局","杨伟森,钟彩华","2019-03-06","1.未对安全设备进行经常性维护、保养和定期检测（B3、B4、C6栋生产车间内三台空压机储气罐安全阀、B4栋生产车间空压机储气罐压力表未定期检测）；2.B3栋生产车间、B4栋生产车间内未划分明显通道标识线；3.B4栋生产车间通道处堆放大量可燃杂物堵塞疏散通道；4.B4栋生产车间部分电源插座未接地、电源线裸露未套管保护；5.B4栋生产车间内部分消火栓、灭火器存在圈占、埋压现象，且未做定期检查；6.B4栋生产车间内氧气、乙炔输送管老旧有裂纹；7.B3、B4栋生产车间内部分电源箱下摆放货物；8.B4栋生产车间配电控制室内摆放杂物、配电柜前缺少防触电绝缘垫；9.C6栋生产车间内设集装箱改装寝室住人，存在二合一现象；10.B4栋生产车间风机房内使用易燃材料进行隔音。","已整改","否"]
[101,"深圳协联塑胶有限公司","英泰工业区10号1-2楼","龙华应急管理局","高扬凯,马征涛","2019-03-07","该企业员工共23名员工，主要生产塑胶配件，执法人员现场检查发现注塑机张贴操作规程，仓库货物已按“五距”要求进行摆放。",null,"否"]
[102,"深圳鸿新晟精密机械配件有限公司","深圳市龙华区观澜街道南大富社区大布头路299号3楼","龙华应急管理局","朱苏宇,陈泰斌","2019-03-07","该企业员工共3名员工，主要生产五金零件加工。",null,"否"]
[103,"深圳市汾水实业有限公司","深圳市龙华区龙华街道东吴工业区5栋B区","龙华应急管理局","翟世明,陈洪星","2019-03-07","1.仓库内消防栓、电箱下堆放货物；2.仓库一处安全出口指示标志缺失；3.仓库阁楼货物堆放过高；4.办公区域内堆放货物；5.仓库内一处安全出口临时锁闭。","整改中","否"]
[104,"深圳鸿恒昌电子有限公司","深圳市龙华新区龙华街道油松水斗旭明工业区B栋2楼","龙华应急管理局","邱定南,陈洪星","2019-03-08","1.未建立事故隐患排查治理制度；2.未将事故隐患排查治理情况如实记录；3.生产车间一台回流焊未安装浓度报警器；4.生产车间防爆柜周围堆放杂物；5.生产车间多名员工（焊锡操作工、刷锡膏操作工）未戴劳保用品。","整改中","否"]
[105,"深圳市宝安区观澜鑫金泉五金网板厂","观澜街道桂花社区惠民一路34号B栋厂房一楼","龙华应急管理局","蔡斌,郭伟雄","2019-03-08","1.机械设备转动齿轮无防护板保护；2.配电箱下方堆放货物及操作空间不足；3.车床设备电气开关裸露、无安装开关盒保护。","整改中","否"]
[106,"深圳市英凌思科技有限公司","深圳市观澜街道大和村597号鑫潮工业区","龙华应急管理局","刘昶麟,邓旭洋","2019-03-08","1.部分电箱未张贴安全警示标志;2.部分焊锡员工未佩戴劳动保护用品;3.部分焊锡岗位无独立抽风;4.防爆柜通风口未扭开，未接地线，未见安全技术说明书;5.危险化学品（工业酒精、洗板水、白电油）存储超过24小时用量。","未复查","否"]
[107,"深圳市沃福特电气有限公司","深圳市龙华区观澜街道牛湖社区石三村82900264号201鸿景鹏工业园","龙华应急管理局","肖龙飞,彭佳亮","2019-03-11","1.变压器接驳端裸露，电源线接驳不完整，2.车间多处使用非国标插排，3.普通日光灯具下方放置可燃物料，易燃物料。","整改中","否"]
[108,"深圳市锦天彩包装有限公司","深圳市龙华新区观澜大坪社区佳怡工业区7号金来旺科技园B栋四楼A区","龙华应急管理局","郑威,肖龙飞","2019-03-11","1、车间部分疏散指示标志损坏未及时更换；2、车间部分电源插座相零线反接；3、车间部分电源开关盒未安装防护盖板；4、车间货物堵塞消防通道。","整改中","否"]
[109,"深圳市皓源电子有限公司","章阁社区章阁社区志扬工业区A栋3F","龙华应急管理局","冼耀行,钟彩华","2019-03-11","1.三楼壳料仓货物堵塞安全疏散通道；2.三楼生产车间有一处工作台未跨接地线保护；3.三楼点胶房安全出口上方未安装应急照明灯及安全出口指示标识。","整改中","否"]
[110,"全一印刷（深圳）有限公司","深圳市龙华区民治街道旭联工业区恒益楼903","龙华应急管理局","陈乃稳,吴建谱","2019-03-12","1.危化品防爆柜未接地保护；2.危化品（洗板水）未粘贴风险告知及安全技术说明；3.防爆柜未建立出入库台账;4.未制定2019年安全生产工作计划。","整改中","否"]
[111,"深圳市贝尔斯通科技有限公司","深圳市龙华新区民治街道民乐工业区2栋205-206","龙华应急管理局","张华城,陈乃稳","2019-03-12","1.仓库通道未划线","整改中","否"]
[112,"深圳市高智创电子有限公司","深圳市龙华新区民治街道民乐工业区2栋407","龙华应急管理局","郑江珠,黄锡山","2019-03-12","1.仓库安全通道堆放办公桌","整改中","否"]
[113,"深圳市美久利电子科技有限公司","深圳市龙华区龙华街道松和社区光辉科技园二栋一单元505","龙华应急管理局","曾繁华,陈洪星","2019-03-12","1.仓库内安全出口门上方未设置应急灯；2.生产车间一处拉线电源插座零火线错误。（","整改中","否"]
[114,"深圳市玛司特电子有限公司","深圳市龙华新区龙华办事处民清路光辉科技园2栋厂房1单元5楼502","龙华应急管理局","邱定南,谢立镇","2019-03-12","1.公司门口摆放大量包装材料；2.一办公室内设焊锡工具混合一体。","整改中","否"]
[115,"深圳弘远电气有限公司","深圳市龙华区龙华街道清湖社区雪岗北路416号A1栋301","龙华应急管理局","邱定南,谢立镇","2019-03-12","1.生产车间焊锡操作工岗位未安装局部排风装置","整改中","否"]
[116,"深圳市正利达五金有限公司","龙华办事处清湖社区安之龙工业区A栋1楼","龙华应急管理局","黄智勇,翟世明","2019-03-12","1.生产车间机器设备无安全操作规程","整改中","否"]
[117,"宏国电子（深圳）有限公司","大坪社区樟企公路企坪佳怡工业区第五栋A楼第二、三层、桂花社区樟企路佳怡工业园14号","龙华应急管理局","陈爱勋,钟文刚","2019-03-12","1、1楼车间排气扇防护罩脱落；2、绗缝机旋转部位未安装防护罩；3、车间部分配电箱体与箱门未跨接地线；4、车间部分电源插座下方堆放可燃物品；5、车间部分电源箱未安装防护隔板；6、杂物间私拉乱接电源线；7、车间部分线槽电线裸露，未加装防护盖板。","整改中","否"]
[118,"美克司电子机械（深圳）有限公司","观澜街道桂花社区樟企路佳怡工业园12号","龙华应急管理局","董善文,陈爱勋","2019-03-12","1、车间砂轮机防护罩损坏未及时更换；2、二楼车间物料放置处上方照明灯具不防爆；3、楼顶高于2米楼梯未安装防护笼；4、宿舍2楼通道安装铁门。","整改中","否"]
[119,"深圳市天防科技有限公司","库坑社区华朗嘉工业园4号401","龙华应急管理局","蔡斌,郑威","2019-03-12","1.保护接地采用缠绕式、接驳、未见接地体，与静电线共用。2.多处插排采用万能插排。3.危险化学品岗位从业人员未佩戴劳动防护用品。4.危险化学品无安全标签，未张贴安全技术说明书。","整改中","否"]
[120,"深圳市力容电子有限公司","深圳市龙华区观澜街道大富社区桂月路300号岭南工业园A栋厂房5层","龙华应急管理局","蔡斌,吴奕霖","2019-03-12","1、生产车间配电开关下方堆放货物；2、含浸车间温湿度管控记录表不全；3、设备实验室部分电线私拉乱接；4、部分消防器材未定期点检记录","整改中","否"]
[121,"深圳世纪百利环保科技有限公司","深圳市龙华新区观澜君龙社区君子布君新工业路6号厂房二楼A区","龙华应急管理局","陈爱勋,董善文","2019-03-12","1.车间后门安全出口未安装应急灯和疏散指示标志；2.车间总配电箱内的分支开关无名称标识；3.车间一处灭火器被货物遮挡；4.陡坡运送货物的区域未张贴安全操作规程；5.一具氧气瓶未设置防倾倒装置；6.一处开关盒上的地线脱落；7.木材堆放区未安装防爆灯","整改中","否"]
[122,"深圳市涵钰服装有限公司","深圳市龙华区观湖街道环观中路370号15栋A401","龙华应急管理局","邓招晴,邱毅彪","2019-03-12","1.生产车间通道被货物堵塞。2.部分用电设备未安装漏电保护开关。","整改中","否"]
[123,"深圳市心迪宝通信设备有限公司","鹏腾达工业园3栋2楼","龙华应急管理局","许伟彬,彭宇新","2019-03-12","1、车间部分焊锡台未安装排烟管；2、车间部分电箱未张贴安全警示标识；3、车间部分配电箱下方堆放杂物；4、仓库货物堆放违反“五距”要求；5、仓库和小储存物料房未安全防爆灯。","整改中","否"]
[124,"深圳市仕诺微自动化有限公司","深圳市龙华新区大浪街道华宁路118号伟杰科技园1栋4楼B区","龙华应急管理局","杨放辉,许爱关","2019-03-12","1.机械设备（洗床）未粘贴操作规程及日常维修保养记录。2.机械设备未粘贴维修风险辨识告知卡。3.部分机械设备末端未安装漏电保护并关。","整改中","否"]
[125,"深圳富皓泽贸易有限公司","龙军工业区第21栋第5层","龙华应急管理局","李进添,庞海锋","2019-03-12","1.仓库未用防火材料分隔到顶。","整改中","否"]
[126,"深圳市和鑫晟智连科技有限公司","深圳市龙华新区大浪街道浪琴路华兴服装产业园园区7号楼2层","龙华应急管理局","许爱关,罗雨锋","2019-03-12","1.部分设备未安装漏电保护开关。\n2.生产车间设办公室存在二合一情况。","整改中","否"]
[127,"深圳市瑞进精密模具有限公司","华兴路富隆特工业区5栋2层","龙华应急管理局","李进添,钟汉林","2019-03-12","经现场核查该企业已搬迁。",null,"否"]