{"text_format":"3","workbook":"xls","n_sheets":2,"sheets":["Sheet1","大浪"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":92,"n_cols":9,"rows_kept":92,"merged":[[0,0,0,8]],"flags":["formulas_cached_only"]}
["龙华应急管理局2019年第六批双随机执法情况公示表"]
["序号","企业名称","企业地址","执法部门","执法人员","检查日期","检查情况（发现隐患问题）","整改情况","是否立案"]
[1,"深圳市伟辉创科技有限公司","深圳市龙华新区大浪办事处同胜社区华荣路联建科技工业园6栋2楼A区","龙华区应急管理局","饶慧彬,钟搌芬","2019-05-13","1.危险品（酒精、洗板水）未设防爆柜存放；2.仓库内设办公设备存在“二合一”现象。","整改中","否"]
[2,"深圳市兴合益盛科技有限公司","深圳市龙华区大浪街道同胜社区石观鸿德工业区B栋501","龙华区应急管理局","张山华,杨放辉","2019-05-13","1、车间灭火器未按要求定时点检，\n2、车间防火门闭门器已损坏。","整改中","否"]
[3,"深圳市果壳科技电子有限公司","深圳市龙华新区大浪街道联润路石观鸿德工业园C栋401","龙华区应急管理局","刘开明,张德兴","2019-05-13","1.该企业已搬迁。","","否"]
[4,"深圳市德金坤科技有限公司","龙华区大浪街道龙强科技园302","龙华区应急管理局","钟汉林,杨放辉","2019-05-13","1.该企业已搬迁。","","否"]
[5,"深圳市瑞兴源科技有限公司","深圳市龙华新区大浪街道谭罗锦泰工业区三栋六楼C区","龙华区应急管理局","陈业明,石元知","2019-04-30","1.该企业已搬迁。","","否"]
[6,"深圳市鑫祥瑞科技有限公司","深圳市龙华区大浪街道华霆路451号恩丰达工业区A栋101号","龙华区应急管理局","吴海志,彭育文","2019-04-26","1、车间部分机械设备（CNC、铣床）未粘贴安全操作规程、日常维修保养记录及风险辨识告知卡；2、铣床，CNC操作工未佩戴劳保用品（耳塞，护目镜）；3、办公室安全出口门未安装安全警示标志及应急照明灯。4、车间安全出口门未安装使用乙级防火门。","整改中","否"]
[7,"深圳市准易美纸品包装有限公司","深圳市龙华区大浪街道水围新村龙达工业园B栋三楼","龙华区应急管理局","许爱关,杨放辉","2019-04-26","1、车间部分机械设备未粘贴安全操作规程、日常维修保养记录及风险辨识告知卡；2、仓库安全出口门使用木质门，需更换乙级防火门；3、车间货物乱放堵塞安全疏散通道；4、车间、仓库混合使用，存在“二合一”现象。","整改中","否"]
[8,"深圳市鑫利五金制品有限公司","黄麻埔工业区108号2楼","龙华区应急管理局","石元知,罗雨锋","2019-04-26","1.该企业已搬迁。","","否"]
[9,"深圳市睿林创意有限公司","深圳市龙华新区大浪街道华宁路明君工业园B1栋1楼","龙华区应急管理局","曾令才,钟汉林","2019-04-25","1.配电箱无警示标志；2.灭火器无保养记录。","整改中","否"]
[10,"深圳市誉辰科技有限公司","大浪白云山永宏丰工业园A栋2楼","龙华区应急管理局","彭宇新,李进添","2019-04-25","1.生产车间设电脑办公。\n2.锡炉台未装贴警示标志。","整改中","否"]
[11,"深圳市隆锋电子科技有限公司","深圳市龙华新区大浪街道浪口金地大科技园D区8栋7楼","龙华区应急管理局","彭宇新,饶慧彬","2019-04-25","1、车间机械设备未张贴安全操作规程及日常维修保养记录；2.车间设空压机，未独立房间使用；3.车间电线乱拉乱接，须调整；4.仓库货物堆放过高，不符合“五距”要求。","整改中","否"]
[12,"深圳市征云途科技有限公司","浪口宝柯工业区1号505","龙华区应急管理局","彭胜勇,钟汉林","2019-04-24","深圳市征云途科技有限公司 ","整改中","否"]
[13,"深圳市集瑞宝科技有限公司","深圳市龙华新区大浪街道浪口工业区宝柯工业园第三栋201","龙华区应急管理局","石元知,钟汉林","2019-04-24","1、仓库货物堆放，不符合“五距”要求；2.碎料房堆放杂物，须立即清理；3.车间电箱下堆放货物，须清理；4.危险化学品分装瓶未张贴安全标签；5.少量电池乱堆放，未规范管理。","整改中","否"]
[14,"深圳玮鸿电子有限公司","深圳市龙华区大浪街道浪口社区金地大科技园A3栋3楼","龙华区应急管理局","庞海锋,许伟彬","2019-04-23","1、车间配电箱（一处）挡板脱落，未跨接；2.黄胶分装瓶未张贴安全标签。","整改中","否"]
[15,"深圳市博恩实业有限公司","深圳市龙华区大浪街道浪口社区华霆路豪迈高新技术园1栋5层、102室102A","龙华区应急管理局","陈业明,黄祖德","2019-04-23","1、五楼办公区域、仓库混合使用存在“二合一”现象；2、五楼部分配电箱未粘贴安全警示标识；3、五楼部分配电箱屏护板缺失且箱体与箱门未作跨接。","整改中","否"]
[16,"深圳市品谦科技有限公司","深圳市龙华区大浪街道浪口河坑工业区瑞信恒业瑞园A3栋2楼","龙华区应急管理局","曾令才,吴海志","2019-04-23","1.车间铣床人员未佩戴劳保用品（护目镜）；2.车间钻床未张贴安全操作规程及日常维修保养记录。","整改中","否"]
[17,"深圳市博日科技有限公司","谭罗村金龙路鸿锦工业区B栋4楼半层","龙华区应急管理局","杨放辉,黄祖德","2019-04-22","1.该企业已搬迁。","","否"]
[18,"深圳汉德霍尔科技有限公司","深圳市龙华区大浪街道潭罗羊台山鸿锦工业区厂房B栋2楼","龙华区应急管理局","胡辉,石元知","2019-04-22","1.防爆柜未设防泄漏拖盘。\n2.老化房测试架未装绝缘胶保护。","整改中","否"]
[19,"深圳市长兴顺科技有限公司","深圳市龙华区大浪街道英泰路143号1栋2楼分隔体","龙华区应急管理局","石元知,陈业明","2019-04-19","1、车间部分电箱未张贴安全警示标志；2、办公出口门使用木门，须换防火门。","整改中","否"]
[20,"深圳市鑫迪科技有限公司","深圳市龙华区福城街道章阁硅谷动力低碳科技示范园A10栋","龙华区应急管理局","杨能鹏,王震","2019-05-09","1.一楼生产车间电钻使用花线；2.二楼仓库灯具不防爆；3.三楼仓库电源控制箱未安装屏护面板；4.二楼、三楼带电工作台金属外壳未接地保护。","整改中","否"]
[21,"深圳市隆利得照明科技有限公司","深圳市龙华区福城街道福民丹湖润塘工业区111栋3楼","龙华区应急管理局","陈耀培,黄国辉","2019-05-09","1.三楼生产车间防火门未安装闭门器；2.三楼生产车间部分电源开关盒损坏内部电源线裸露；3.三楼生产车间工作台金属部分未静电接地。","整改中","否"]
[22,"深圳市博亿方电子有限公司","福民狮径冼屋工业一路4栋3号2楼（港银厂内）","龙华区应急管理局","吴宏宇,陈坚华","2019-05-08","1.二楼生产车间押出机转轮危险部位未安装防护罩；2.二楼生产车间灭火器未落实定期检查并记录。","整改中","否"]
[23,"深圳市佳虎精密科技有限公司","深圳市龙华区福成街道大水坑一村桔路77号厂房五整套1栋5楼B区","龙华区应急管理局","庄志江,宋煜竹","2019-05-08","1.生产车间部分电源控制开关下发堆放杂物，未留操作空间。","已整改","否"]
[24,"深圳市言果科技有限公司","深圳市龙华区福城街道大水坑社区大三村621号金鑫鹏厂房五101","龙华区应急管理局","巫静成,陈志成","2019-05-06","1.一楼机加工车间有一处电源开关插座未接地线；2.一楼机加工车间有一处电源控制开关盒未张贴安全警示标识；3.一楼机加工车间部分机械设备维修保养记录未及时记录。","整改中","否"]
[25,"深圳市盈百川科技有限公司","大三村金湖湾23号1栋2楼","龙华区应急管理局","冼耀行,陈志成","2019-05-06","1.一楼锂电池仓库采用木卡板存放锂电池；2.一楼锂电池仓库电源线未作防爆措施；3.配电房门未采用甲级防火门，灭火器未定期检查（4月未检查）。","整改中","否"]
[26,"深圳市全路安科技有限公司","深圳市龙华新区观澜街道福城办事处章阁社区章阁老村东区166号松源创新科技城D5楼西南边厂房","龙华区应急管理局","罗兆麟,李宏桃","2019-05-06","该企业已搬迁","该企业已搬迁","否"]
[27,"深圳市合和塑胶有限公司","大二村合和科技园4栋2楼201","龙华区应急管理局","宋煜竹,黄志航","2019-04-30","1.碎料机外壳无接地保护；\n2.部分注塑机炮筒（高温区域）无安全警示标志；\n3.仓库未安“五距”摆放，且缺少安全警示标志（当心火灾,严禁烟火）","整改中","否"]
[28,"深圳市智仁科技有限公司","章阁边园山工业路","龙华区应急管理局","黄志航,陈耀培","2019-04-26","1.整形车间安全出口上方未安装应该照明灯和灯光疏散指示标志；\n2.部分消防栓、灭火器材未张贴标识标牌；\n3.插件车间带电工作台灯具电线裸露未入槽保护；\n4.一楼插件车间、二楼组装车间防爆柜设置不合理，通风口未打开，未接地线，未张贴安全技术说明书，未张贴责任人信息；","整改中","否"]
[29,"深圳市自立五金制品有限公司","福民福前路盛景源工业园七栋","龙华区应急管理局","莫雪宁,罗兆麟","2019-04-18","1.一楼生产车间两台冲床（012、013）双手同步按钮损坏；2.未对安全设备（储气罐压力表、安全阀）进行经常性维护、保养和定期检测；3.三楼手工丝印房两窗口未用实体墙密封，无安装可燃气体浓度报警器并与防爆风机连锁；4.三楼涂层烘干室抽排风管道破损。","整改中","是"]
[30,"深圳市鼎兴数控科技有限公司","深圳市龙华区福城街道茜坑新城社区旭日大楼B栋三楼北边","龙华区应急管理局","陈科铭,巫静成","2019-04-18","1.三楼生产车间总电源箱未安装屏护板；2.三楼生产车间地面未实施划线；3.三楼生产车间数控精雕机粉尘未定时清理；4.三楼生产车间与仓库设置在同一区域，未进行防火分隔。5.未建立事故隐患排查治理制度；6.未按照规定对从业人员进行安全生产教育和培训。","已整改","是"]
[31,"深圳市伟正润五金塑胶制品有限公司","粮食集团工业园区10栋A一层部分厂房","龙华区应急管理局","邓旭洋,吴能猛","2019-05-10","1.部分电箱前堆放物料;\n2.冲床齿轮未加密处理。","整改中","否"]
[32,"深圳市汉鹏科技有限公司","深粮集团A9栋3楼","龙华区应急管理局","林耿宇,廖志城","2019-05-10","1.部分电箱未安装屏护板;\n2.车间存在吸烟现象;\n3.灭火器、消防栓前堆放货物。","整改中","否"]
[33,"深圳市兴世源科技有限公司","深圳市龙华区观湖街道新田社区腾龙工业区103号林格公司2栋厂房201","龙华区应急管理局","邓旭洋,苗隆","2019-05-10","1.部分电源开关保护盖缺失，且无标签;\n2.灭火器配备不均匀，且无检查记录;\n3.冲床未进行固定处理。","整改中","否"]
[34,"深圳市文宝鑫包装制品有限公司","麒麟工业区2号2楼","龙华区应急管理局","陈镇江,陈小龙","2019-05-10","1.灭火器前堆放货物;\n2.部分电箱保护盖缺失;\n3.电箱下堆放货物。","整改中","否"]
[35,"深圳市鸿誉陶玻原料股份有限公司","深圳市龙华区观湖街道南大富社区环观中路222号4楼401","龙华区应急管理局","何嘉敏,唐飞","2019-05-09","一、部分出口无安全出口灯；二、部分化学品分装容器无安全标签；三、部分灭火器未按时点检。","整改中","否"]
[36,"深圳市效利工程设备有限公司","创新工业区118栋厂房3楼A区","龙华区应急管理局","苗隆,何嘉敏","2019-04-30","1.配电箱无安全警示标志；2.配电箱箱门未跨接地线；3.灭火器无2019年点检记录。","整改中","否"]
[37,"深圳市海德威视科技有限公司","龙华区观湖街道大和社区大和村573号7楼东区","龙华区应急管理局","陈嘉威,廖志城","2019-04-30","1.未进行2019年安全生产培训。","整改中","否"]
[38,"深圳市龙华区观湖新杰成塑胶加工厂","金茂路28号好景厂房旁边","龙华区应急管理局","唐飞,梁华保","2019-04-26","1.车间电箱下堆放货物；\n2.车间员工未佩戴劳保用品（耳塞）；\n3.车间使用移动插座不符合新国标；\n4.落地扇网孔过大。","整改中","否"]
[39,"深圳乐包环保包装制品有限公司","深圳市龙华区观湖街道观城社区美华城工业区B栋302","龙华区应急管理局","叶嘉丽,彭锡山","2019-04-23","1、临时仓库“五距”要求不够；2、部分员工未佩戴劳保用品；3、配电箱未安装二级漏电保护开关，无屏护挡板；4、部分线路未套管；","整改中","否"]
[40,"深圳市精美旭电子科技有限公司","观光路1073号东达工业园1栋3楼","龙华区应急管理局","陈子东,叶嘉丽","2019-04-22","1.办公区域与生产车间未分开设置，存在“二合一”现象；2.堆放货物地面未划线；3.部分灭火器未悬挂稳固，无更新点检记录；4.配电箱未安装二级漏电保护开关。","整改中","否"]
[41,"深圳市健益五金制品有限公司","深圳市龙华区观湖街道樟坑径社区白鸽湖路83号201","龙华区应急管理局","胡基立,林耿宇","2019-04-22","1、未完善2019年安全生产管理制度；2、部分线路裸露未套管保护。","整改中","否"]
[42,"深圳市顺捷瑞机械有限公司","虎地排一楼","龙华区应急管理局","林耿宇,邓志远","2019-04-22","1、车间安全通道未按要求划线；2、部分机器设备没有张贴安全操作规程；3、部分电源开关没有张贴安全警示标志；4、配电箱没有设防护栏；5、攻牙机未加固使用；6、CNC没有张贴定期清扫记录；7、灭火器没有按要求存放。","整改中","否"]
[43,"深圳市三能机电设备有限公司","下湖社区天棚工业园二栋1楼103","龙华区应急管理局","张富城,唐飞","2019-04-19","1.部分气瓶未做固定措施；2.电箱内电源开关无漏电保护开关；3.电焊操作岗位与电源开关箱距离不足。","整改中","否"]
[44,"深圳市舒雅静家纺有限公司","深圳市龙华新区观澜街道松元社区上围新村86栋一二楼","龙华区应急管理局","彭锡山,阳虎田","2019-04-19","1.灭火器配备不足；2.部分电源线未套管保护；3.仓库货物堆放过高，不符合五距要求；4.部分衣车无漏电保护开关；5.车间未划线,消防通道堵塞；6.部分出口无应急灯、安全出口标志。","整改中","否"]
[45,"深圳市六合欣精密五金有限公司","深圳市龙华区观湖街道松元社区昌玮工业园区299号4楼电梯后","龙华区应急管理局","陈镇江,吴能猛","2019-04-18","1、生产车间员工未佩戴劳动保护用品。2、车间部分机械安全防护不足。3、车间部分机械未张贴安全操作规程。4、空压机旁堆放杂物。5、消防栓下货物堵塞。6、仓库安全通道未划线。7、仓库未安装防爆灯。8、车间电源箱下电线裸露。9、未建立金属废屑定期清扫记录。","整改中","否"]
[46,"深圳市宇讯达电子有限公司","下湖社区天棚工业园二栋1楼103","龙华区应急管理局","叶嘉丽,刘昶麟","2019-04-18","1.部分气瓶未做固定措施；2.电箱内电源开关无漏电保护开关；3.电焊操作岗位与电源开关箱距离不足。","整改中","否"]
[47,"深圳市炫音族科技有限公司","深圳市龙华新区观澜办事处大布巷社区对面2-1号三楼A区","龙华区应急管理局","张寿强,郑威","2019-05-13","1、车间插座电源线未穿管保护，流水线金属线槽无盖板。2、车间焊锡岗位无排风裝置,作业员工未佩戴防护口罩。3、仓库防爆灯电源线穿管不全。4、仓库内使用大功率电热水器。","整改中","否"]
[48,"深圳市益合兴科技有限公司","深圳市龙华区观澜街道桂香社区金业工业区8号401","龙华区应急管理局","张寿强,彭佳亮","2019-05-13","1、车间灭火器堵塞、圈占；2、丝印车间可燃气体浓度报警装置故障未及时维修；3、防爆柜内盛装化学品的容器未张贴安全标签；4、丝印车间电气线路未整体防爆；5、杂物间部分电源线裸露，未套管安装；6、部分电源排插损坏未及时更换。","整改中","否"]
[49,"智隆包装（深圳）有限公司","牛湖新湖路23号厂房","龙华区应急管理局","郭伟雄,董善文","2019-05-08","1.安全出口卷闸门未加装防坠落措施。2.车间部分电线裸露，未套管保护。3.车间大功率电风扇电源线接驳。4.啤机日常维护保养记录未及时更新，摇杆保护装置失灵。5.分纸机防护措施安装不到位。6.生产车间货物堆放过多。7.车间使用非国标插排。8.总配电箱箱体与箱门跨接线用线错误。9.车间安全出口门上方安全出口指示灯失效。","整改中","否"]
[50,"深圳市汇涛模具有限公司","深圳市龙华新区观澜石马径社区石新路3000054号二楼B区","龙华区应急管理局","郑威,张寿强","2019-05-08","1.车间卷闸门未做防坠落措施。2.注塑机、铣床机身电源插座无接地线。3.低于2.4米以下金属工作台未做接地保护。4.注塑机加料梯台未做防护措施。5.防锈剂、脱模剂放置于设备高温部位，未妥善管理。6.行车吊钩防脱钩装置破损未及时更换。7.多台注塑机电源线入孔处未做保护，套管不到位，且为可燃材质，机身外壳接地线断开。8.所有设备未设置日常维护保养记录。9.车间配电箱箱体与箱门未做跨接。10.手持电动工具电源线多处接驳。11.车间办公区域多处使用非国标插排，且无接地线。12.仓库防火门不符合相应的耐火等级。","整改中","否"]
[51,"深圳佳思提科技有限公司","深圳市龙华新区观澜星花社区品顺路134号日技城1号厂房2楼204号205号","龙华区应急管理局","杨文辉,吴奕霖","2019-05-07","1、车间化学品未存放在防爆柜内；2、车间部分电源开关盒挡板缺失，未及时修复；3、车间部分岗位使用非国标排插；4、吊装口未张贴“小心坠落”标识。","整改中","否"]
[52,"深圳市德为兴包装有限公司","观澜街道桂花路340号厂房三楼A区","龙华区应急管理局","彭佳亮,杨文辉","2019-05-07","1、防爆柜内存放的化学品无安全技术说明书；2、车间部分线槽破损，未及时更换；3、平板打印机无日常设备维护保养记录表。","整改中","否"]
[53,"深圳市精典印务有限公司","观澜富坑社区大富工业区3号厂房三、一层","龙华区应急管理局","郭伟雄,张寿强","2019-05-07","1.生产车间防爆柜周边堆放货物；2.生产车间电源开关箱损坏；3.生产车间印刷机设备防护盖缺失；4.油墨等化学品未设置专门存放点随意乱放；5.生产车间部分电源开关未安装漏电保护装置；6.生产车间使用泡沫夹芯门。","整改中","否"]
[54,"途曼电源（深圳）有限公司","观澜街道凹背社区大富工业区20号硅谷动力智能终端产业园A12栋第1层A面、第4层","龙华区应急管理局","钟文刚,吴奕霖","2019-05-07","1.生产车间自动烤箱未安装漏电保护装置；2.生产车间自动烤箱设备的防护盖缺失；3.生产车间锡焊岗位未安装抽排风设施，且员工未佩戴劳保用品；4.生产车间部分岗位使用非国标排插；5.电池仓位未安装温湿度监测装置；6.停用实验设备电池未进行有效处理。","整改中","否"]
[55,"深圳市锦诺科技有限公司","牛湖君新路鸿景鹏工业园c栋3楼","龙华区应急管理局","郑威,陈锦润","2019-05-06","1.车间部分开关电源线裸露，未套管保护到位。2.仓库安全出口门上方未安装应急灯具及安全疏散指示标志。3.开关盒线路凌乱，部分线路外露未套管保护，且使用非国标插排。4.车间多处使用非国标插排，且无接地线。5.车间多个移动风扇电源线接驳、不完整 。6.热收缩机未张贴醒目的“注意高温”、“当心烫伤”等安全警示标志，未设置日常维护保养记录。7.回转旋熔机双手按钮开关不同步。8.仓库未设置“禁止烟火”、“禁止吸烟”等安全指示标志。9.钻床等设备未设置安全操作规程及日常维护保养记录。10.车间多个功能区域防火门为泡沫材质填充。","整改中","否"]
[56,"深圳市德全盛电子科技有限公司","澜凹背社区桂月路334号同富裕工业园A6栋4楼B面","龙华区应急管理局","董善文,陈锦润","2019-05-06","1.化学品未设置固定存放点，随意乱放；2.生产车间化学品使用普通饮料瓶分装；3.生产车间多处使用非国标排插； 4.端子机电机接线裸露； 5.生产车间电源开关盒损坏和防护盖缺失；6生产车间操作台照明灯电源线裸露未套管保护；7.仓库货物靠墙堆放；8.在厕所旁进行染色作业；9.锡焊岗位未设置职业危害告知卡；10.未在有较大危险因素的生产经营场所和有关设施、设备上设置明显的安全警示标志。","整改中","是"]
[57,"深圳市希水硅橡胶有限公司","深圳市龙华区观澜街道大水田社区大水田0500056号201","龙华区应急管理局","陈爱勋,郑威","2019-04-22","1、现场未见化学品（背胶胶水）MSDS安全技术说明书。2、车间金属工作台外壳未设置“PE”跨接。3、拌料机设备危险区域未加装防护罩。4、车间内电源线存在简易接驳现象。5、车间电源开关盒缺失。6、车间二级电源箱未装屏护挡板","已整改","否"]
[58,"深圳市协盛泰五金塑胶有限公司","深圳市龙华区观澜街道大水田社区大水田0100030号101","龙华区应急管理局","陈爱勋,蔡斌","2019-04-19","1、碎料机转动危险区域缺失保护罩。2、车间二级电箱未加装屏护挡板。3、行车起重设备未粘贴明显的安全警示标志。","已整改","否"]
[59,"深圳市恒邦滤清器制品有限公司"," 深圳市龙华新区龙华街道华联社区阁吓工业区鸿鹏飞实业101五栋（一至三层）","龙华区应急管理局","陈洪星,张键","2019-05-10","1、一楼落地扇护网间隙过大。2、一处安全门闭门器损坏。3、生产车间砂轮机作业区域未独立间隔且无整套除尘系统。","整改中","否"]
[60,"深圳市兴开泰包装制品有限公司","龙华区清湖安之龙工业区B栋3楼","龙华区应急管理局","章胜旗,邱定南","2019-05-10","1.未将事故隐患排查治理情况如实记录;2.未按照规定对从业人员进行安全生产教育和培训;3.生产车间多台机器设备未按照漏电保护器;4.生产车间机器设备无安全操作规程;5.仓库货物摆放不符合“五距”要求。","整改中","否"]
[61,"深圳市欣代光电有限公司","深圳市龙华区龙华街道建辉路82号富联工业园2栋4楼","龙华区应急管理局","曾繁华,谢立镇","2019-05-09","1.仓库使用不防爆电气设备（日光灯）;2.生产车间机器设备（封口机）未安装漏电保护器。\n","整改中","否"]
[62,"深圳安格仪器有限公司","深圳市龙华区龙华街道和平工业园丽彩大厦五楼A区","龙华区应急管理局","陈洪星,张键","2019-05-09","1.生产车间焊锡操作岗位未安装局部排风装置;2.未按照规定对从业人员进行安全生产教育和培训。\n","整改中","否"]
[63,"深圳市齐力达包装材料有限公司","深圳市龙华新区大浪南路墩背工业区1栋4楼","龙华区应急管理局","张键,黄智勇","2019-05-08","1、机器设备维修保养记录未定期更新。2、冲床设备作业人员未佩戴劳保用品（耳塞）。3、未将2019年度安全培训工作纳入本单位工作计划并保证安全培训工作所需资金的问题。","整改中","是"]
[64,"巨圳(深圳)科技有限公司","深圳市龙华区龙华街道富康社区建进工业区D栋2楼东侧","龙华区应急管理局","翟世明,谢立镇","2019-05-07","1.仓库安全出口门为普通木质门；2.公司一向安全出口门上班时被货物封堵；3.未建立安全生产责任制；4.未建立事故隐患排查治理制度；5.未制定事故应急救援预案；6.未将安全培训计划纳入本公司本年度的工作计划（检查时未制定安全培训计划与公司工作计划）7.未按规定对从业人员进行安全培训教育。","整改中","是"]
[65,"深圳市华星发科技有限公司","深圳市龙华新区龙华大浪南路老围第二工业区A栋5楼","龙华区应急管理局","林跃辉,张键","2019-04-26","1、生产车间一处通道堆放货物。2、贴合机维修保养记录未定期更新。3、未按规定对从业人员进行安全教育和培训(未开展2019年从业人员安全教育和培训)。","整改中","否"]
[66,"深圳百里木商贸有限公司","龙华街道清湖新碑村36栋一楼（联丰泰工业园2楼B区）","龙华区应急管理局","林跃辉,张键","2019-04-22","1、未按规定对从业人员进行安全教育培训（2019年开年至今未对从业人员进行安全教育和培训）。","整改中","否"]
[67,"深圳倍思优科技有限公司","民乐科技园统建楼2栋1605","龙华区应急管理局","杨洋,吴建谱","2019-05-13","1.仓库货物摆放混乱","整改中","否"]
[68,"深圳市罗丹贝尔科技有限公司","民乐工业区创意大厦502、503","龙华区应急管理局","赵吉飞,杨洋","2019-05-13","1.埋压消防灭火器材","整改中","否"]
[69,"深圳市吉格士科技有限公司","民乐工业园E栋201","龙华区应急管理局","张机敏,杨洋","2019-05-13","1、办公区域堆放货物","整改中","否"]
[70,"深圳市龙华新区龙华一声喊照明店","民治街道第五工业区南2巷4号A栋301","龙华区应急管理局","张机敏,陈育平","2019-05-09","该公司进行检查时发现公司已搬迁",null,"否"]
[71,"深圳市佰诺威家具有限公司","深圳市龙华区民治街道亚伯工业区B栋4楼","龙华区应急管理局","黄锡山,吴建谱","2019-05-09","公司现场正在进行装修施工作业，已到相关部门报备",null,"否"]
[72,"深圳市凯伦美电子有限公司","深圳市龙华区民治街道上芬社区第五工业区一区79号301","龙华区应急管理局","余焕森,余俊贤","2019-05-07","1、仓库灭火器未按规定定时检查；2、该公司已对员工进行安全生产培训并留下相关记录。","整改中","否"]
[73,"深圳市梦之韵文化传媒有限公司","深圳市龙华牛栏前工业区26栋101","龙华区应急管理局","董启茂,张华城","2019-04-29","1、已配备应急照明灯及灭火器材",null,"否"]
[74,"深圳市励志光科技有限公司","泰明工业区2栋4楼","龙华区应急管理局","赵吉飞,张华城","2019-04-29","1、仓库货物摆放混乱不符合“五距”要求。2、安全出口处未安装应急照明灯。3、仓库内未配备足够的灭火器材。","整改中","否"]
[75,"深圳市吉运泰饰品有限公司","深圳市龙华新区民治上塘第五工业区亚柏工业园A栋303","龙华区应急管理局","谢栓,林正权","2019-04-29","1、生产车间灭火器定期点检；2、已进行员工的安全教育培训",null,"否"]
[76,"深圳市优乐易购电子商务有限公司","泰明工业区1栋1楼C区","龙华区应急管理局","魏文浩,张文龙","2019-04-29","1、仓库主要通道画线不明显。2、隐患排查治理情况及安全培训情况不完善。","整改中","否"]
[77,"深圳市艺速快印有限公司","深圳市龙华新区民治街道民治大道973号万众润丰创业园二档","龙华区应急管理局","赵吉飞,张华城","2019-04-22","1.防爆柜内油墨清洗剂存量过多；2.防爆柜内堆放杂物；3.防爆柜内油墨清洗剂未粘贴安全技术说明书，未制定出入库台账；4.机械设备未制定维护保养记录；5.机械设备末端电源开关未安装漏电保护器；6.车间内一应急照明灯破损；7.灭火器未定期检查。","已整改","否"]
[78,"深圳市拓柏科技有限公司","深圳市龙华新区民治街道民乐工业区1栋303","龙华区应急管理局","张机敏,张华城","2019-04-18","已配备消防灭火器材",null,"否"]
[79,"深圳市新奇顺纺织品有限公司","深圳市龙华新区民治街道民乐工业区1栋602","龙华区应急管理局","陈乃稳,钱俊崇","2019-04-18","1、办公区域堆放货物","已整改","否"]
[80,"深圳市通联网络商务有限公司","深圳市龙华新区民治街道溪山美地园一期2栋30D","龙华区应急管理局","张华城,黄锡山","2019-04-18","1、已配备应急照明灯及灭火器材",null,"否"]
[81,"深圳市乐闪光电有限公司","深圳市龙华新区民治民乐工业园D栋6楼","龙华区应急管理局","张华城,吴建谱","2019-04-18","1、隐患排查排查治理情况（照片不完善）2、烧录机未制定操作规程","已整改","否"]
[82,"深圳市君安宏图技术有限公司","深圳市龙华区民治街道上芬社区第五工业区一区22号201","龙华区应急管理局","张华城,董启茂","2019-04-18","1.生产车间内配电开关下方堆放可燃物品；2.办公室安全疏散通道堆放杂物；3.灭火器未定期点检；4.配电房内堆放杂物。","已整改","否"]
[83,"深圳市晟亚五金制品有限公司","深圳市龙华新区大浪街道三合新村高创德工业园6号A栋406","龙华区应急管理局","陈中明,符桓彬","2019-04-26","1、部分设备电线未套管保护，使用花线； 2、部分设备未张贴安全操作规程；3、冲压设备未为员工配备护目镜；4、一台磨床未设置安全防护罩。","整改中","否"]
[84,"深圳市雅力佳印刷有限公司","深圳市龙华大浪街道华霆路307号永乐华a栋5楼东","龙华区应急管理局","刘勤,简丹","2019-04-26","1、原材料仓库五距不符合要求，仓库内设置生产作业设备（封条机），不符合要求；2、生产车间商标机及模切机未张贴安全生产作业操作规程（或作业指导书）；3、部分插座未接地线。","整改中","否"]
[85,"深圳市亿锦光电有限公司","深圳市龙华区观澜街道桂花社区惠民一路30号301","龙华区应急管理局","高扬凯,郭文忠","2019-05-08",null,"无隐患","否"]
[86,"深圳市原创自动化设备有限公司","深圳市龙华新区观澜街道君子布凌屋工业路4号A栋1楼","龙华区应急管理局","孙汉林,王斌富","2019-05-08",null,"无隐患","否"]
[87,"深圳市路威五金制品有限公司","深圳市龙华区观湖街道观澜新田沙博工业园17号","龙华区应急管理局","朱苏宇,赖嘉杰","2019-05-07","1、特种作业操作人员（焊工，阳锋）未持证上岗作业；2、配电箱箱门与箱体之间未进行跨接；3、电气插座不符合现行国家标准，且零火线序错误；4、电开关盒盖板损坏；5、部分灭火器报废，设置不符合规范标准。","整改中","是"]
[88,"恒超源洗净科技（深圳）有限公司","深圳市龙华新区观澜街道牛湖社区石一村2800098号201","龙华区应急管理局","傅霏,付凌敏","2019-05-07",null,"无隐患","否"]
[89,"深圳市楚枫利化工有限公司","深圳市龙华新区大浪街道华霆路119号宿舍一楼(潮回楼）","龙华区应急管理局","朱剑峰,廖名玙","2019-05-06","1、一楼仓库未按要求配备灭火器、明显处无禁烟防火警示标志；2、通道堆放杂物；3、办公室电源插座未按要求安装地线。4、办公室使用国家已淘汰的电源插排。","整改中","否"]
[90,"深圳中深星光家具有限公司","深圳市龙华新区观澜街道牛湖石二村新湖路38号","龙华区应急管理局","黄熔,胡甘雨","2019-04-29","1.一楼仓库货物摆放墙距不足，不符合“五距”要求；2.仓库灭火器直接放地上，且无点检记录；3.仓库灯具未做防爆处理。","整改中","否"]

{"sheet":"大浪","index":1,"n_rows":19,"n_cols":11,"rows_kept":19,"flags":["formulas_cached_only"]}
["22","SSJ-深龙华2019399","深圳市伟辉创科技有限公司","大浪办事处安监办","饶慧彬,钟搌芬","2019-05-13","执法检查","2019-06-07","","否",""]
["40","SSJ-深龙华2019395","深圳市兴合益盛科技有限公司","大浪办事处安监办","张山华,杨放辉","2019-05-13","执法检查","2019-06-21","","否",""]
["43","SSJ-深龙华2019394","深圳市果壳科技电子有限公司","大浪办事处安监办","刘开明,张德兴","2019-05-13","执法检查","","","否",""]
["53","SSJ-深龙华2019400","深圳市德金坤科技有限公司","大浪办事处安监办","钟汉林,杨放辉","2019-05-13","执法检查","2019-06-07","","否",""]
["425","SSJ-深龙华2019354","深圳市瑞兴源科技有限公司","大浪办事处安监办","陈业明,石元知","2019-04-30","执法检查","","","否",""]
["538","SSJ-深龙华2019367","深圳市鑫祥瑞科技有限公司","大浪办事处安监办","吴海志,彭育文","2019-04-26","执法检查","2019-05-26","","否",""]
["539","SSJ-深龙华2019360","深圳市准易美纸品包装有限公司","大浪办事处安监办","许爱关,杨放辉","2019-04-26","执法检查","2019-05-31","","否",""]
["546","SSJ-深龙华2019344","深圳市鑫利五金制品有限公司","大浪办事处安监办","石元知,罗雨锋","2019-04-26","执法检查","","","否",""]
["617","SSJ-深龙华2019340","深圳市睿林创意有限公司","大浪办事处安监办","曾令才,钟汉林","2019-04-25","执法检查","2019-06-02","","否",""]
["623","SSJ-深龙华2019339","深圳市誉辰科技有限公司","大浪办事处安监办","彭宇新,李进添","2019-04-25","执法检查","2019-06-03","","否",""]
["624","SSJ-深龙华2019338","深圳市隆锋电子科技有限公司","大浪办事处安监办","彭宇新,饶慧彬","2019-04-25","执法检查","2019-06-02","","否",""]
["767","SSJ-深龙华2019337","深圳市征云途科技有限公司","大浪办事处安监办","彭胜勇,钟汉林","2019-04-24","执法检查","2019-06-02","","否",""]
["811","SSJ-深龙华2019336","深圳市集瑞宝科技有限公司","大浪办事处安监办","石元知,钟汉林","2019-04-24","执法检查","2019-06-01","","否",""]
["856","SSJ-深龙华2019335","深圳玮鸿电子有限公司","大浪办事处安监办","庞海锋,许伟彬","2019-04-23","执法检查","2019-05-31","","否",""]
["933","SSJ-深龙华2019331","深圳市博恩实业有限公司","大浪办事处安监办","陈业明,黄祖德","2019-04-23","执法检查","2019-05-23","","否",""]
["944","SSJ-深龙华2019333","深圳市品谦科技有限公司","大浪办事处安监办","曾令才,吴海志","2019-04-23","执法检查","2019-05-31","","否",""]
["1020","SSJ-深龙华2019325","深圳市博日科技有限公司","大浪办事处安监办","杨放辉,黄祖德","2019-04-22","执法检查","","","否",""]
["1029","SSJ-深龙华2019323","深圳汉德霍尔科技有限公司","大浪办事处安监办","胡辉,石元知","2019-04-22","执法检查","2019-05-31","","否",""]
["1042","SSJ-深龙华2019327","深圳市长兴顺科技有限公司","大浪办事处安监办","石元知,陈业明","2019-04-19","执法检查","2019-05-28","","否",""]