{"text_format":"3","workbook":"xls","n_sheets":1,"sheets":["Sheet1"],"not_rendered":{"external_links":1,"defined_names":1},"read":"whole","date_system":"1900","formulas":"cached_only"}

{"sheet":"Sheet1","index":0,"n_rows":76,"n_cols":9,"rows_kept":76,"merged":[[0,0,0,8]],"flags":["formulas_cached_only"]}
["龙华应急管理局2019年第八批双随机执法情况公示表"]
["序号","企业名称","企业地址","执法部门","执法人员","检查日期","检查情况（发现隐患问题）","整改情况","是否立案"]
[30,"深圳市盛世传奇文化发展股份有限公司","深圳市龙华区民治街道民治社区1970文化创意园C栋103","民治街道安监办","赵吉飞,杨洋","2019-06-24","未对企业从业人员进行安全教育和培训。","整改中","否"]
[31,"深圳市精禾化工有限公司","深圳市龙华新区民治街道梅龙路与民旺路相交处民治商贸广场（七星商业广场）B座1306","民治街道安监办","张华城,钟国峰","2019-06-24","1.未按规定配备安全出口指示牌和应急救援照明灯；2.未按规定粘贴安全用电警示标识。","整改中","否"]
[62,"深圳市中科巨龙科技有限公司","深圳市龙华新区龙华油松华雅工业园","龙华办事处安监办","林跃辉,陈洪星","2019-06-24","经现场核查发现该企业已关闭",null,"否"]
[63,"深圳泰和精密电子有限公司","龙华区/龙华街道办事处/清华社区","龙华办事处安监办","黄智勇,张键","2019-06-24","1、焊锡工位员工未佩戴劳动保护用品（口罩）。2、未按规定对从业人员进行安全教育和培训（缺少培训课时）。","整改中","否"]
[90,"深圳市迦南科技有限公司","深圳市龙华区福城街道福民丹湖康脉工业区2栋1楼","福城街道办安监办","罗中宝,陈俊荣","2019-06-24","1.生产车间气瓶区未张贴警示标志；2.一台移动风扇未接地保护；3.配电箱附近堆放杂物；4.部分机械设备未张贴风险告知卡、维修保养记录；5.一台电焊机未安装末端漏电保护开关；6.生产车间一侧出口疏散指示标志已损坏。","整改中","否"]
[91,"深圳市龙华区观澜鸿盛胶袋店","深圳市龙华区福城街道茜坑四和社区茜坑路65号1楼","福城街道办安监办","黄国辉,陈科铭","2019-06-24","1.一楼生产车间部分电源插座地线接地故障；2.一楼生产车间部分电源开关盒保护盖缺失；3.一楼仓库货物随意堆放，不符合“安全五距”要求。","整改中","否"]
[107,"逸晨（深圳）光电有限公司","大浪街道新石社区同富邨工业区4栋4楼","大浪办事处安监办","张德兴,饶慧彬","2019-06-24","1.磨边机未建立粉尘清扫记录表，2.部分机械设备未安装漏电保护开关，3.消泡机无操作规程，无保养记录。","整改中","否"]
[140,"深圳市俊达捷电气实业有限责任公司","观澜街道高尔夫大道133号宝商盈工业区A栋101","观澜街道办事处安监办","张寿强,郭伟雄","2019-06-24","1.车间卷闸门未做防坠落措施。2.个别临时电源插座及母线加工机机身插座无接地线。3.多台切割设备及钻床末端未安装漏电保护开关。4.个别移动风扇电源线未连接地线。5.砂轮机未安装挡屑板及托架，砂轮机开口朝向通道，6.个别氩弧焊机未接地保护。7.个别氩弧焊机电源线裸露。8.油漆、自动喷漆随处放置，未妥善存放及管理。9.钻床、切割设备未设置安全操作规程及日常维护保养记录。10.办公区域使用非国标插排。","整改中","否"]
[1,"深圳市新中鸣包装制品有限公司","深圳市龙华区观湖观城横坑社区金祥工业区B栋一楼102","观湖街道办安监办","陈文达,唐飞","2019-06-21","1、车间二级剩余电流保护装置缺失；2、部分车间通道被货物占用；3、部分货物堆放不规范，高处货物有倾倒危险。","整改中","否"]
[64,"深圳市杰少实业有限公司","深圳市龙华新区龙华街道龙观路龙华电子市场2B037","龙华办事处安监办","谢立镇,陈洪星","2019-06-21","经现场核查发现该企业已搬迁",null,"否"]
[92,"深圳市博荣自动化技术开发有限公司","福民丹湖润塘工业区（景隆泰2楼）","福城街道办安监办","李宏桃,杨能鹏","2019-06-21","1.二楼生产车间部分电源插座安装在可燃材料（木板）上；2.二楼生产车间卷圆机转动轴未加装保护罩；3.二楼生产车间氩弧焊焊机末端未安装漏电保护开关。","整改中","否"]
[93,"深圳市聚力德智能发展有限公司","深圳市龙华区福城街道桔塘社区章阁路36号勋立科技园A栋101","福城街道办安监办","陈俊荣,黄国辉","2019-06-21","1.一楼仓库内设置办公桌办公，存在二合一现象；2.二楼生产车间部分防火门未安装闭门器。","整改中","否"]
[2,"深圳市华顶电子材料制品有限公司","观湖街道新田社区腾龙工业区94号101","观湖街道办安监办","陈文达,陈嘉威","2019-06-20","1、车间部分通道未划分；2、部分设备未张贴相关维修保养记录；3、部分电源插座未接地线保护。","整改中","否"]
[3,"深圳市亚盛达塑胶制品有限公司","第三工业区盈丰路1号4栋1楼","观湖街道办安监办","陈镇江,邱毅彪","2019-06-20","1.部分灭火器过期及保养记录；2.大功率落地扇网孔过大；3.车间部分电线未套管保护；4.车间吊臂防脱落装置损坏；5.货物堆放过高。","整改中","否"]
[4,"深圳市创智科贸电子有限公司","深圳市龙华区观湖街道新田村环观南路越兴8工业园D栋2楼","观湖街道办安监办","叶英龙,邓翠芬","2019-06-20","该公司由深圳市观湖街道新田社区越兴8工业园D栋2楼搬迁至东莞，搬迁地不属于观湖街道辖区。","已搬迁","否"]
[32,"深圳市趣科学教育咨询有限公司","民治街道龙屋工业区Yan创园4楼405A","民治街道安监办","郑江珠,魏文浩","2019-06-20","经现场核查发现该企业已搬迁",null,"否"]
[108,"深圳市欣瑞兴螺丝五金有限公司","深圳市龙华区大浪街道高峰社区元芬工业区F栋102","大浪办事处安监办","杨远辉,杨放辉","2019-06-19","1、仓库电气（灯具）未作防爆处理；2、生产车间机械设备未张贴相关操作规程及维修保养记录；3、生产车间部分电线使用花线。","整改中","否"]
[109,"深圳市达欧沃科技有限公司","大浪街道高峰社区元芬工业区B区512室","大浪办事处安监办","钟汉林,胡辉","2019-06-19","1、仓库货物堆放过高，须调整；2、仓库电气（灯具）未作防爆处理；3、办公区域堆放货物，存在“二合一”现象。","整改中","否"]
[141,"深圳市益源佳电子有限公司","第六工业区新石桥街3号3楼（羽思凡旁）","观澜街道办事处安监办","钟文刚,陈爱勋","2019-06-18","1.未建立事故隐患排查治理制度；2.危化品使用饮料瓶盛装及无张贴安全标签；3.危化品（助焊剂）未配备专用防爆柜存放；4.仓库安全出口门未安装闭门器设施；5.烤箱设备未张贴安全操作规程；6.车间使用电源插座非国标；7.绕线机皮带无设置防护罩保护。","整改中","否"]
[142,"深圳市森力生贸易有限公司","深圳市龙华新区观澜街头牛湖大水田工业A区欣时雅制品厂内","观澜街道办事处安监办","郑威,钟文刚","2019-06-18","1、车间电源线存在简易接驳现象。2、车间二级电箱箱门未设置“PE”跨接线。3、车间安全疏散通道未规范划线。4、防爆柜周边堆放杂物、可燃物。5、车间切割工艺存在积水现象，电器线路未穿管到位。","整改中","否"]
[143,"深圳市展楠科技有限公司","深圳市龙华区观澜街道君龙社区龙兴第一工业区5号厂房B栋3楼G区","观澜街道办事处安监办","陈锦润,钟文刚","2019-06-18","1.车间工作台上的使用已淘汰的“万能插座”；2.车间安全出口的防火门闭门器失效。","整改中","否"]
[144,"深圳市民润环保科技有限公司","深圳市龙华区观澜街道桂花社区桂花路113号201、202","观澜街道办事处安监办","郭伟雄,钟文刚","2019-06-18","1.未建立事故隐患排查治理制度；2.安全出口后门未安装闭门器及应急灯等设施；3.卷闸门未设置防坠落装置；4.车间电源插座及仓库出口应急灯设施脱落；5.疏散通道未设应急灯和安全指示标识；6.防爆柜未张贴安全技术说明书及责任牌；7.仓库内设置焊锡岗位；8.疏散通道和电气开关周边堆放物品。","整改中","否"]
[168,"深圳美科博电科技有限公司","深圳市大浪街道元芬工业园D栋3楼","龙华区应急管理局","朱苏宇,叶钟灵","2019-06-18","无隐患",null,"否"]
[5,"深圳市宏彰纸艺包装有限公司","盈丰路6-1号301","观湖街道办安监办","黄桂明,吴能猛","2019-06-17","1.电线裸露未套管；2.灭火器未定期维护保养；3.啤机未粘贴操作规程；4.使用塑胶瓶分装危险化学品（白电油）；5.抹机水粘贴警示标志不规范；6.气枪头摆放位置过高；7.电箱屏护板无静电跨接。","整改中","否"]
[6,"深圳市美嘉华精密机电有限公司","深圳市龙华新区观澜街道岗头社区第三工业区金茂路19号B座202","观湖街道办安监办","陈家雄,陈永仁","2019-06-17","1、气枪随意摆放；2、部分灭火器未定期维护保养；3、消防栓下堆放杂物；4、大功率风扇未安装屏护网；5、部分钻床未固定。","整改中","否"]
[7,"瑞阳达科技有限公司","深圳市龙华新区观澜街道老村社区新怡街27号5楼","观湖街道办安监办","陈小龙,张富城","2019-06-17","1.仓库内货物堆放不规范；2.员工未佩戴口罩作业。","整改中","否"]
[65,"深圳市富安娜家居用品股份有限公司龙华工厂","龙华街道清湖工业区富安娜工业园","龙华办事处安监办","翟世明,谢立镇","2019-06-17","经现场核查发现该企业已搬迁",null,"否"]
[94,"深圳市合信精密机械有限公司","深圳市龙华区福城街道大三社区大三村642号鑫源工业区一楼五区","福城街道办安监办","陈志成,刘杭科","2019-06-17","经现场核查发现该企业已搬迁",null,"否"]
[110,"深圳市万方圆印刷包装有限公司","大浪安丰工业区E栋一楼","大浪办事处安监办","饶慧彬,许爱关","2019-06-17","1.部分电源开关未张贴安全警示标志。2.仓库部分墙体未使用砖墙分隔到顶及未安装防火门。3.防爆柜未张贴安全管理人员信息。4.印刷机上方灯具未作防爆处理。5.车间、仓库混合使用，存在“二合一”现象。5.啤机未使用双脚踏板保护，且正常使用。","整改中","否"]
[111,"丽港实业(深圳)有限公司","深圳市龙华区大浪街道谭罗工业区1栋1-4楼","大浪办事处安监办","黄祖德,曾育凯","2019-06-17","1、车间防爆柜责任人信息不健全;2、部分机械设备未粘贴安全操作规程和维修保养记录;3、车间照明灯具低于2M以下未安装独立保护开关;4、配电柜周边杂物圈占需搬离。","整改中","否"]
[112,"深圳市广信达科技发展有限公司","深圳市龙华区大浪街道同富裕工业区21栋6楼605厂房","大浪办事处安监办","石元知,吴海志","2019-06-17","经现场核查发现该企业已搬迁","","否"]
[113,"深圳市龙华区大浪爱情鸟表业加工厂","深圳市龙华区大浪街道同胜社区联恒工业区D栋403号","大浪办事处安监办","罗宝贵,邓国鸿","2019-06-17","经现场核查发现该企业已搬迁","","否"]
[114,"深圳市海利鑫科技有限公司","深圳市龙华区大浪街道潭罗路33号锦泰工业区1栋4楼","大浪办事处安监办","许爱关,吴加良","2019-06-17","经现场核查发现该企业已搬迁","","否"]
[115,"深圳显仕科技有限公司","深圳市龙华新区大浪街道华辉路73号C栋626","大浪办事处安监办","张德兴,罗宝贵","2019-06-17","1、焊锡台未安装排烟管道2、货物堵塞安全疏散通道","整改中","否"]
[116,"深圳市齐兴行商贸有限公司","深圳市龙华新区大浪街道鹊山佳利工业区第三栋二楼","大浪办事处安监办","易子焯,练志成","2019-06-17","1.仓库内所有电源开关未张贴安全警示标志。2.楼梯间堆放杂物，未作清理。","整改中","否"]
[117,"深圳市合万盛实业有限公司万盛百货大浪中心店","深圳市宝安区大浪街道同胜社区华旺路同富裕工业园内A栋1-2楼","大浪办事处安监办","杨放辉,彭宇新","2019-06-17","1、冻库配电箱未安装独立漏电被保护开关2、部分配电箱未粘贴防触电警示标示","整改中","否"]
[118,"深圳市鑫源通精密有限公司","罗屋围第三工业区D栋1、2楼东","大浪办事处安监办","刘开明,曾令才","2019-06-17","经现场核查发现该企业已搬迁","","否"]
[119,"深圳泰科特科技有限公司","深圳市龙华区大浪街道新石社区华宁路42号港深创新园A栋503-506","大浪办事处安监办","周锡展,吕芳华","2019-06-17","1、危险品分装容器未张贴标签，2、危险品防爆柜未张贴技术说明书。","整改中","否"]
[120,"深圳市图雅丽特种技术有限公司","深圳市龙华新区大浪街道华宁路东龙兴工业园6栋5-6楼","大浪办事处安监办","胡辉,李进添","2019-06-17","经现场核查发现该企业已搬迁","","否"]
[121,"深圳市嘉鸿宝科技有限公司","大浪北路默根工业园A栋12楼","大浪办事处安监办","易子焯,彭宇新","2019-06-17","1、工作台瓶子未张贴标签","整改中","否"]
[122,"深圳市嘉兰德科技有限公司","深圳市龙华区大浪街道华兴工业区7栋4楼","大浪办事处安监办","钱志成,幸小东","2019-06-17","经现场核查发现该企业已搬迁","","否"]
[145,"深圳市鑫久同包装材料有限公司","深圳市龙华区观澜街道君龙社区凌屋工业区10号厂房1栋","观澜街道办事处安监办","陈锦润,郭伟雄","2019-06-17","1.一楼仓库内一处配电箱中的分支开关无名称标识。2.一楼仓库内的液压打包机未安装漏电保护开关。3.一楼仓库内的疏散通道被货物堵塞。4.一楼破碎机进料口的防护挡板破损。5.一楼破碎机电机部位堆放可燃物品（塑胶废料）。6.一楼破碎机的喂料平台过高，不符合人体工程学相关要求。7.一楼仓库内的货物堆放不符合“五距”要求。8.一楼仓库内的配电箱被货物遮挡。9.宿舍一楼饭堂内违规放置电动车。10.保安室内的电动车存放处未设置自动灭火装置。11.消防水泵自动控制箱内的电线未套管，电子元件老化，箱体锈蚀。12.一楼一处配电柜围栏未锁闭，未张贴联系人信息卡。13.配电房地面电缆沟槽未设置密封盖板。14.配电房内未配置劳保用品（绝缘靴、绝缘棒、绝缘手套等）。15.配电房门口未设置挡鼠板。16.车间进线管道破损。","整改中","否"]
[146,"深圳市金鸿盛橡塑制品有限公司","深圳市龙华区观澜街道牛湖木头湖新村72号","观澜街道办事处安监办","陈爱勋,董善文","2019-06-17","经现场核查发现该企业已搬迁",null,"否"]
[8,"深圳市宝创达电子有限公司","深圳市龙华区观湖街道横坑河西老村77号A栋2楼","观湖街道办安监办","梁华保,廖志城","2019-06-14","1.车间部分电箱未张贴警示标志；2.逃生出口未张贴安全出口指示牌。","整改中","否"]
[66,"深圳市龙华区龙华街道宜成五金加工部","深圳市龙华区龙华街道和平工业园D栋2楼","龙华办事处安监办","张键,翟世明","2019-06-14","1、砂轮机未独立间隔。2、落地扇护网间隙过大。","整改中","否"]
[95,"深圳市诚美纸业有限公司","深圳市龙华区福城街道新塘村荣富路37号安龙强工业园第1栋","福城街道办安监办","吴宏宇,刘杭科","2019-06-14","经现场核查发现该企业已搬迁",null,"否"]
[67,"深圳市希可尔科技有限公司","深圳市龙华区建辉路82号富联工业园二期1栋四楼","龙华办事处安监办","林跃辉,谢立镇","2019-06-13","1、测试车间电线路乱拉乱接。2、焊锡工位无警示标识。3、防爆柜危化品出入库未及时更新。","整改中","否"]
[68,"深圳市仙童微电子有限公司","深圳市龙华新区龙华大浪南路联围街2号A栋3楼","龙华办事处安监办","翟世明,谢立镇","2019-06-13","1.部分安全出口无应急灯；2.不分消防设施被杂物围挡；3.部分氮气瓶无防倾倒装置；4.生产车间机器设备无维保记录。","整改中","否"]
[147,"深圳市骏宏泰五金制品有限公司","深圳市宝安区观澜街道大布巷社区大坑龙四黎路恒兴园D栋一楼","观澜街道办事处安监办","郑威,杨文辉","2019-06-13","1、车间配电箱箱门接地线缠绕连接。2、车间工业风扇无地线，电源线护套不全。3、磨床无防护套罩，无安全操作规程。4、台钻皮带轮无防护罩。5、日光灯电源线有接驳。","整改中","否"]
[33,"深圳市铭扬电气有限公司","沙吓工业区10栋3楼303","民治街道安监办","房智锋,余俊贤","2019-06-12","经现场核查发现该企业已搬迁",null,"否"]
[96,"深圳市康威达电子有限公司","深圳市龙华区福城街道章阁社区上塘新村26号1号厂房，2号厂房","福城街道办安监办","王震,罗中宝","2019-06-12","1.一楼、二楼楼梯间通道堵塞；2.部分机械设备防护罩缺失；3.一处插座未接地保护；4.两处配电箱未安装屏护板，配电箱内地线未跨接；5.部分机械设备未张贴安全警示标识、风险告知卡、维修保养记录、安全操作规程。","整改中","否"]
[97,"深圳聚广和科技有限公司","深圳市龙华区福城街道章阁社区章阁老村东区128号金和瑞瑚琳工业园A栋101","福城街道办安监办","罗中宝,黄国辉","2019-06-12","1.仓库货物上方灯具不防爆；2.酒精分装瓶未张贴安全标签；3.车间部分设备未张贴安全警示标识；4.1楼车间磨床防护罩缺失。","整改中","否"]
[98,"深圳市华联威电子科技有限公司","福民润塘工业区","福城街道办安监办","巫静成,江志豪","2019-06-12","1.一楼冲压车间部分金属架工作台插头未接地线；2.一楼冲压车间润滑油盛装容器未张贴安全标签；3.一楼冲压车间部分金属架工作台插排相零线接反；4.二楼组装车间部分金属架工作台未做地线跨接；5.三楼仓库通道出口处堆放货物堵塞疏散通道。","整改中","否"]
[99,"深圳市天基权健康科技产业园管理有限公司","福民富康工业区A31栋","福城街道办安监办","江志豪,王震","2019-06-12","1.一楼维修部金属架工作台未接地保护；2.一楼维修部金属架工作台未设置漏电保护开关；3.一楼报废仓库出口处未设置应急灯及安全出口标志。","整改中","否"]
[9,"深圳市志邦纸品包装有限公司","深圳市龙华区观湖街道樟坑径社区上围工业一路4号栋401","观湖街道办安监办","汪宏,邓翠芬","2019-06-11","1.过胶机热熔位置未张贴相关警示标志（2处）；2.多处插板杆未固定好；3.物品堆放过高，部分到顶，且存在二合一现象。","整改中","深龙华2019901"]
[34,"深圳市三一九科技有限公司","深圳市龙华区民治街道梅龙路宝山工业区A8栋5楼东","民治街道安监办","黄锡山,杨洋","2019-06-11","经现场核查发现该企业已搬迁",null,"否"]
[35,"深圳市宝安区民治骏盛电子厂","泰明工业区三栋四楼","民治街道安监办","谢栓,张文龙","2019-06-11","已开展企业事故隐患自查自改",null,"否"]
[36,"深圳市百汇安防电子有限公司","深圳市龙华新区民治街道工业东路南侧泰明工业区三栋第五层B区","民治街道安监办","钱俊崇,钟国峰","2019-06-11","仓库、车间未按规定配备安全出口指示标志及应急灯","整改中","否"]
[37,"深圳市好事多物联网有限公司","深圳市民治街道宇丰工业区2栋4楼西北","民治街道安监办","黄锡山,陈育平","2019-06-11","已对员工进行安全生产教育培训.仓库内货物堆放整齐",null,"否"]
[69,"深圳林兴光学科技有限公司","深圳市龙华区龙华街道伍屋科技园2栋3楼A区","龙华办事处安监办","曾繁华,翟世明","2019-06-11","经现场核查发现该企业已搬迁",null,"否"]
[38,"深圳市惠园物业管理有限公司","深圳市龙华新区民治街道深惠工业园B栋2楼","民治街道安监办","郑江珠,张文龙","2019-06-10","安全培训记录不完善","已整改","否"]
[70,"深圳新太开发科技有限公司","中裕冠大道7号院3层","龙华办事处安监办","张键,陈洪星","2019-06-10","1.老化房内存放可燃货物；2.生产车间安全疏散通道堆放货物；3.未对新进员工进行安全培训教育并建档记录。","整改中","否"]
[71,"淘福（深圳）环境科技有限公司","深圳市龙华新区龙华街道清宁路彩煌大厦5楼501室","龙华办事处安监办","林跃辉,章胜旗","2019-06-10","1.办公室内堆放货物;2.仓库使用不防爆电器（日光灯）。","整改中","否"]
[72,"深圳市好一生电子科技有限公司","深圳市龙华新区龙华街道油松大道东侧宜德行工业厂区厂房B第5-6层","龙华办事处安监办","谢立镇,陈洪星","2019-06-10","经现场核查发现该企业已搬迁",null,"否"]
[10,"易麦斯电子材料有限公司","鸿鹏飞工业园A栋1楼B","观湖街道办安监办","许斌宇,周伟","2019-06-06","1.生产车间违规停放电动车（已现场整改）；2.空压机气喷枪头放置不规范。","整改中","否"]
[11,"深圳智尚视讯科技有限公司","深圳市龙华新区观澜景田路观澜创新工业园N栋4楼","观湖街道办安监办","周伟,张艺馨","2019-06-06","1.焊锡岗位部分员工未佩戴口罩；2.未张贴焊锡工位职业病危害告知卡。","整改中","否"]
[12,"深圳博鑫兴五金制品有限公司","深圳市龙华区观湖街道樟坑径社区仙湖牛角龙工业区A7栋三楼","观湖街道办安监办","陈文达,陈嘉威","2019-06-06","1.高温水池未张贴高温警示标志；2.烤箱前堆放货物；3.安全出口被货物堵塞。","整改中","否"]
[13,"深圳市深华科科技有限公司","观澜章坑经下围工业区1路6号","观湖街道办安监办","梁华保,宋增","2019-06-06","1.部分电源箱无屏护板，且未夸接地线；2.车间内瓶装危险化学品未张贴警示标识；3.出口堆放货物堵塞消防通道。","整改中","否"]
[39,"深圳兆瑞分析仪器有限公司","民治街道中华路1号康盛电子产业园C栋307-310","民治街道安监办","林正权,陈育平","2019-06-06","已对从业人员进行安全生产教育培训并留下相关记录",null,"否"]
[73,"深圳市鼎兴数控设备有限公司","深圳市龙华新区清祥路清湖科技园B栋351室","龙华办事处安监办","章胜旗,谢立镇","2019-06-06","1.生产车间一台烤箱未安装漏电保护开关（此项已改正）;2.防爆柜内防火棉缺失（此项已改正）。","已整改","否"]
[74,"深圳市力欣自动化有限公司","大和路凤天创新科技产业园11楼1128-1131","龙华办事处安监办","曾繁华,邱定南","2019-06-06","1、生产车间焊锡岗位未安装局部排风装置（此项已改正）；2、生产车间一处电源开关零线、火线相位错位（此项已改正）。","已整改","否"]
[100,"深圳微星博科技有限公司","深圳市龙华区福城街道福民社区丹湖润塘工业区34号2楼","福城街道办安监办","陈坚华,陈志成","2019-06-06","1.二楼生产车间部分2.4米以下照明灯及工作台金属架构部分未进行接地保护；2.二楼生产车间机械设备未张贴设备风险告知卡、维修保养记录及安全操作规程；3.二楼生产车间焊锡岗位员工未佩戴符合国家或行业标准的劳保用品（口罩）；4.二楼空压机房部分电源插座未进行接地保护；5.二楼生产车间部分大功率电风扇存在电源线路裸露现象且未进行接地保护。","整改中","否"]
[148,"深圳市旭诚泰硅橡胶模具制品有限公司","观澜街道牛湖社区新湖路82号102 ","观澜街道办事处安监办","蔡斌,杨文辉","2019-06-06","1.手持电动工具电源线多处接驳。2.车间卷闸门未做防坠落措施。3.多台磨刀机局部照明电压为220V，一台磨刀机末端未安装漏电保护开关。4.神龛照明电源线为单层绝缘，未套管保护。5.多台设备电源线套管不到位，部分电源线裸露。6.车间多处使用非国标插排。","整改中","否"]
[149,"深圳市兴钜泰硅橡胶有限公司","深圳市龙华新区观澜街道牛湖老村东方红工业园2栋1楼","观澜街道办事处安监办","郭伟雄,吴奕霖","2019-06-06","1、车间多处使用淘汰非国标排插；2、火花机机械设备转动部位保护罩缺失；3、车间安全出口应急指示灯失效；4、CNC机台机械设备后面存放化学品液压油未定制管理；5 、车间电源盒开关处电源线未套管保护到顶","已整改","否"]